MOD Form 2207

VISUAL, CLOSE & DETAILED INSPECTIONS SPECIFIC TO CATEGORY A, B AND DSEAR ZONES

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - VISUAL INSPECTION |
| Check that: | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| EQUIPMENT |  |  |  |  |  |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |  |  |
| Equipment circuit identification is available |  |  |  |  |  |
| Installation is clearly labelled |  |  |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |  |  |
| There are no visible unauthorised modifications |  |  |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |  |  |
| - visual check |  |  |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |  |  |
| INSTALLATION |  |  |  |  |  |
| There is no obvious damage to cables |  |  |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |  |  |
| - physical check |  |  |  |  |  |
| - visual check |  |  |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |  |  |
| Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14 |  |  |  |  |  |
| ENVIRONMENT |  |  |  |  |  |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |  |  |
| No undue external accumulation of dust and dirt |  |  |  |  |  |
| Note 1: The checks used for equipment using both types of protection "e" and "d" will be a combination of both columns. |
| Note 2: Account shall be taken of the possibility of an explosive atmosphere in the vicinity of the equipment when using electrical test equipment. |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY B & DSEAR ZONES 20, 21 and 22 - VISUAL INSPECTION |
| Check that: | Ex "iD" | Ex "pD" | Ex "tD" |
| EQUIPMENT |  |  |  |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |
| IP grade of equipment is appropriate to conductivity of dust |  |  |  |
| Equipment circuit identification is available |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |
| There are no unauthorized modifications |  |  |  |
| There are no visible unauthorised modifications |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |
| - visual check |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |
| INSTALLATION |  |  |  |
| The installation is such as to minimise the risk of dust accumulations |  |  |  |
| There is no obvious damage to cables |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |
| - visual check |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |
| ENVIRONMENT |  |  |  |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |
| No undue external accumulation of dust and dirt |  |  |  |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

REMEDIAL ACTIONS ARISING FROM VISUAL INSPECTIONS SPECIFIC TO CATEGORY A, B AND DSEAR ZONES

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Classification Codes

Each observation relating to a concern about the safety of the installation shall be attributed an appropriate Classification Code selected from the standard codes C1, C2 and C3 as follows:

Code C1	‘Danger present’ Risk of injury. Immediate remedial action required

Code C2	‘Potentially dangerous’ Urgent remedial action required

Code C3	‘Improvement recommended’

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - CLOSE INSPECTION (Page 1 of 2) |
| Check that: | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| EQUIPMENT |  |  |  |  |  |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |  |  |
| Equipment group is correct |  |  |  |  |  |
| Equipment installed is that specified in the documentation - Fixed equipment only |  |  |  |  |  |
| Equipment temperature class is correct |  |  |  |  |  |
| Circuit and/or equipment category and group correct |  |  |  |  |  |
| Equipment circuit identification is available |  |  |  |  |  |
| Installation is clearly labelled |  |  |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |  |  |
| There are no visible unauthorised modifications |  |  |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |  |  |
| - physical check |  |  |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |  |  |
| Flange gap dimensions are within maximal values permitted |  |  |  |  |  |
| INSTALLATION |  |  |  |  |  |
| There is no obvious damage to cables |  |  |  |  |  |
| Cable screens are earthed in accordance with the documentation |  |  |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |  |  |
| - physical check |  |  |  |  |  |
| - visual check |  |  |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |  |  |
| Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14 |  |  |  |  |  |
| Variable voltage/frequency installation in accordance with documentation |  |  |  |  |  |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - CLOSE INSPECTION (Page 2 of 2) |
| ENVIRONMENT | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |  |  |
| No undue external accumulation of dust and dirt |  |  |  |  |  |
| Note 1: The checks used for equipment using both types of protection "e" and "d" will be a combination of both columns. |
| Note 2: Account shall be taken of the possibility of an explosive atmosphere in the vicinity of the equipment when using electrical test equipment. |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

REMEDIAL ACTIONS ARISING FROM CLOSE INSPECTIONS SPECIFIC TO CATEGORY A, AND DSEAR ZONES 0, 1 & 2

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Classification Codes

Each observation relating to a concern about the safety of the installation shall be attributed an appropriate Classification Code selected from the standard codes C1, C2 and C3 as follows:

Code C1	‘Danger present’ Risk of injury. Immediate remedial action required

Code C2	‘Potentially dangerous’ Urgent remedial action required

Code C3	‘Improvement recommended’

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - DETAILED INSPECTION (Page 1 of 3) |
| Check that: |  |  |  |  |  |
| EQUIPMENT | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |  |  |
| Equipment group is correct |  |  |  |  |  |
| Equipment installed is that specified in the documentation - Fixed equipment only |  |  |  |  |  |
| Equipment temperature class is correct |  |  |  |  |  |
| Circuit and/or equipment category and group correct |  |  |  |  |  |
| Equipment circuit identification is correct |  |  |  |  |  |
| Equipment circuit identification is available |  |  |  |  |  |
| Installation is clearly labelled |  |  |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |  |  |
| There are no unauthorized modifications |  |  |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |  |  |
| - physical check |  |  |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |  |  |
| Flange faces are clean and undamaged and gaskets, if any, are satisfactory |  |  |  |  |  |
| Electrical connections are tight |  |  |  |  |  |
| Flange gap dimensions are within maximal values permitted |  |  |  |  |  |
| Printed circuit boards are clean and undamaged |  |  |  |  |  |
| Lamp rating, type and position are correct |  |  |  |  |  |
| Electrical connections are tight |  |  |  |  |  |
| Conditions of enclosure gaskets is satisfactory |  |  |  |  |  |
| Enclosed-break and hermetically sealed devices are undamaged |  |  |  |  |  |
| Restricted breathing enclosure is satisfactory |  |  |  |  |  |
| Motor fans have sufficient clearance to enclosure and/or covers |  |  |  |  |  |
| Breathing and draining devices are satisfactory |  |  |  |  |  |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - DETAILED INSPECTION (Page 2 of 3) |
| Check that: | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| INSTALLATION |  |  |  |  |  |
| Type of cable is appropriate |  |  |  |  |  |
| Cables are installed in accordance with the documentation |  |  |  |  |  |
| There is no obvious damage to cables |  |  |  |  |  |
| Cable screens are earthed in accordance with the documentation |  |  |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |  |  |
| There is no obvious damage to cables |  |  |  |  |  |
| Stopping boxes and cable boxes are correctly filled |  |  |  |  |  |
| Integrity of conduit system and interface with mixed system is maintained |  |  |  |  |  |
| Point-to-point connections are all correct |  |  |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |  |  |
| - physical check |  |  |  |  |  |
| Earth continuity is satisfactory (e.g. connections are tight, conductors are of sufficient cross-section) for non-galvanised isolated circuits |  |  |  |  |  |
| Fault loop impedance (TN systems) or earthing resistance (IT systems) is satisfactory |  |  |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |  |  |
| Protective gas inlet temperature is below maximum specified |  |  |  |  |  |
| Insulation resistance is satisfactory |  |  |  |  |  |
| Intrinsically safe circuit earthing and insulation resistance is satisfactory |  |  |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |  |  |
| Automatic electrical protective devices operate within permitted limits |  |  |  |  |  |
| Separation is maintained between intrinsically safe and non-intrinsically safe circuits in common distribution boxes or relay cubicles |  |  |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |  |  |
| Automatic electrical protective devices are set correctly (auto-reset not possible) |  |  |  |  |  |
| As applicable, short-circuit protection of the power supply is in accordance with the documentation |  |  |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |  |  |
| Specific conditions of use (if applicable) are complied with |  |  |  |  |  |
| Pressure and/or flow indicators, alarms and interlocks function correctly |  |  |  |  |  |
| Cables not in use are correctly terminated |  |  |  |  |  |
| Conditions of spark and particle barriers of ducts for exhausting the gas in hazardous area are satisfactory |  |  |  |  |  |
| Obstructions adjacent to flameproof flanged joints are in accordance with IEC 60079-14 |  |  |  |  |  |
| Variable voltage/frequency installation in accordance with documentation |  |  |  |  |  |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY A & DSEAR ZONES 0, 1 and 2 - DETAILED INSPECTION (Page 3 of 3) |
| Check that: | Ex "d" | Ex "e" | Ex "n" | Ex "i" & "nL" | Ex "p" |
| ENVIRONMENT |  |  |  |  |  |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |  |  |
| No undue external accumulation of dust and dirt |  |  |  |  |  |
| Electrical insulation is clean and dry |  |  |  |  |  |
| Note 1: The checks used for equipment using both types of protection "e" and "d" will be a combination of both columns. |
| Note 2: Account shall be taken of the possibility of an explosive atmosphere in the vicinity of the equipment when using electrical test equipment. |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

REMEDIAL ACTIONS ARISING FROM DETAILED INSPECTIONS SPECIFIC TO CATEGORY A AND DSEAR ZONES 0, 1 & 2

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY B & DSEAR ZONES 20, 21 and 22 - CLOSE INSPECTION |
| Check that: | Ex "d" | Ex "e" | Ex "n" |
| EQUIPMENT |  |  |  |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |
| IP grade of equipment is appropriate to conductivity of dust |  |  |  |
| Equipment group is correct |  |  |  |
| Equipment installed is that specified in the documentation - Fixed equipment only |  |  |  |
| Equipment maximum surface temperature is correct |  |  |  |
| Circuit and/or equipment category and group correct |  |  |  |
| Equipment circuit identification is available |  |  |  |
| Installation is clearly labelled |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |
| There are no visible unauthorised modifications |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |
| - physical check |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |
| INSTALLATION |  |  |  |
| The installation is such as to minimise the risk of dust accumulations |  |  |  |
| There is no obvious damage to cables |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |
| - visual check |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |
| Cables not in use are correctly terminated |  |  |  |
| ENVIRONMENT |  |  |  |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |
| Note 1: The checks used for equipment using both types of protection "e" and "d" will be a combination of both columns. |
| Note 2: Account shall be taken of the possibility of an explosive atmosphere in the vicinity of the equipment when using electrical test equipment. |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

REMEDIAL ACTIONS ARISING FROM CLOSE INSPECTIONS SPECIFIC TO CATEGORY B AND DSEAR ZONES 20, 21 & 22

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Classification Codes

Each observation relating to a concern about the safety of the installation shall be attributed an appropriate Classification Code selected from the standard codes C1, C2 and C3 as follows:

Code C1	‘Danger present’ Risk of injury. Immediate remedial action required

Code C2	‘Potentially dangerous’ Urgent remedial action required

Code C3	‘Improvement recommended’

If required the following inspections shall be carried out in addition to the visual and close inspections undertaken in Jobs 1 & 2

| Site: | Building: |
| --- | --- |
| CATEGORY B & DSEAR ZONES 20, 21 and 22 - DETAILED INSPECTION (Page 1 of 2) |
| Check that: | Ex "iD" | Ex "pD" | Ex "tD" |
| EQUIPMENT |  |  |  |
| Equipment is appropriate to the EPL/Zone requirements of the location |  |  |  |
| Circuit and/or equipment documentation is appropriate to the EPL/zone requirements of the location |  |  |  |
| IP grade of equipment is appropriate to conductivity of dust |  |  |  |
| Equipment group is correct |  |  |  |
| Equipment installed is that specified in the documentation - Fixed equipment only |  |  |  |
| Equipment maximum surface temperature is correct |  |  |  |
| Circuit and/or equipment category and group correct |  |  |  |
| Equipment circuit identification is correct |  |  |  |
| Equipment circuit identification is available |  |  |  |
| Installation is clearly labelled |  |  |  |
| Enclosure, glass(es) parts and glass-to-metal sealing gaskets and/or compounds are satisfactory |  |  |  |
| There are no unauthorized modifications |  |  |  |
| There are no visible unauthorised modifications |  |  |  |
| Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight |  |  |  |
| - physical check |  |  |  |
| Safety barrier units, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required |  |  |  |
| Printed circuit boards are clean and undamaged |  |  |  |
| Lamp rating, type and position are correct |  |  |  |
| Electrical connections are tight |  |  |  |
| Conditions of enclosure gaskets is satisfactory |  |  |  |
| Motor fans have sufficient clearance to enclosure and/or covers |  |  |  |
| Breathing and draining devices are satisfactory |  |  |  |
| INSTALLATION |  |  |  |
| The installation is such as to minimise the risk of dust accumulations |  |  |  |
| Type of cable is appropriate |  |  |  |
| Cables are installed in accordance with the documentation |  |  |  |
| There is no obvious damage to cables |  |  |  |
| Cable screens are earthed in accordance with the documentation |  |  |  |
| Sealing of trunking, ducts, pipes and/or conduits is satisfactory |  |  |  |
| There is no obvious damage to cables |  |  |  |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

| Site: | Building: |
| --- | --- |
| CATEGORY B & DSEAR ZONES 20, 21 and 22 - DETAILED INSPECTION (Page 2 of 2) |
| Check that: | Ex "iD" | Ex "pD" | Ex "tD" |
| Point-to-point connections are all correct |  |  |  |
| Earthing connections, including any supplementary earthing bonding connections are satisfactory (for example connections are tight and conductors are of sufficient cross-section) |  |  |  |
| - physical check |  |  |  |
| Earth continuity is satisfactory (e.g. connections are tight, conductors are of sufficient cross-section) for non-galvanised isolated circuits |  |  |  |
| Fault loop impedance (TN systems) or earthing resistance (IT systems) is satisfactory |  |  |  |
| Earth connections maintain the integrity of the type of protection |  |  |  |
| Protective gas inlet temperature is below maximum specified |  |  |  |
| Insulation resistance is satisfactory |  |  |  |
| Intrinsically safe circuit earthing and insulation resistance is satisfactory |  |  |  |
| Ducts, pipes and enclosures are in good condition |  |  |  |
| Automatic electrical protective devices operate within permitted limits |  |  |  |
| Separation is maintained between intrinsically safe and non-intrinsically safe circuits in common distribution boxes or relay cubicles |  |  |  |
| Protective gas is substantially free from contaminants |  |  |  |
| Automatic electrical protective devices are set correctly (auto-reset not possible) |  |  |  |
| As applicable, short-circuit protection of the power supply is in accordance with the documentation |  |  |  |
| Protective gas pressure and/or flow is adequate |  |  |  |
| Specific conditions of use (if applicable) are complied with |  |  |  |
| Pressure and/or flow indicators, alarms and interlocks function correctly |  |  |  |
| Cables not in use are correctly terminated |  |  |  |
| Conditions of spark and particle barriers of ducts for exhausting the gas in hazardous area are satisfactory |  |  |  |
| ENVIRONMENT |  |  |  |
| Equipment is adequately protected against corrosion, weather, vibration and other adverse factors |  |  |  |
| No undue accumulation of dust and dirt |  |  |  |
| Note 1: The checks used for equipment using both types of protection "e" and "d" will be a combination of both columns. |
| Note 2: Account shall be taken of the possibility of an explosive atmosphere in the vicinity of the equipment when using electrical test equipment. |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate

(	To indicate an inspection has been carried out and the result is satisfactory

X	To indicate an inspection was unsatisfactory

N/A	To indicate an inspection is not applicable

REMEDIAL ACTIONS ARISING FROM DETAILED INSPECTIONS SPECIFIC TO CATEGORY B AND DSEAR ZONES 20, 21 & 22

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Classification Codes

Each observation relating to a concern about the safety of the installation shall be attributed an appropriate Classification Code selected from the standard codes C1, C2 and C3 as follows:

Code C1	‘Danger present’ Risk of injury. Immediate remedial action required

Code C2	‘Potentially dangerous’ Urgent remedial action required

Code C3	‘Improvement recommended’