## Space List
ADM02 | Interview room | Room off reception area for meetings with visitors without the need to access the main school | 6 | ADM02 (Interview room)
ADM05 | General office (1 recep desk) | Main office for administrative staff, with reception desk for visitors, off entrance/ reception area | As SoA | ADM05 (General office (1 re...
ADM08 | Reprographics room | Room for reprographics and photocopying machines | 20 | ADM08 (Reprographics room)
ADM11 | Head's office | Office for head teacher | 16 | ADM11 (Head s office)
OFF01 | Small 1-person office | Office for one member off staff, with admin storage | 7 | OFF01 (Small 1-person office)
OFF12 | Medium 2-person office | Office for two members of staff, with space for meetings | 9 | OFF12 (Medium 2-person office)
OFF23 | Office (SENco) | Office for SENco and team | 12 | OFF23 (Office (SENco))
OFF32 | Staff room (social) | Main space for any staff in school to meet and socialise | As SoA | OFF32 (Staff room (social))
OFF33 | Staff work room | Space for staff in [school or suite] to work and meet | As SoA | OFF33 (Staff work room)
OFF41 | Conference/ meeting room | Conference room for meetings of staff, governors and other adults | 20 | OFF41 (Conference and meeti...
RES02 | Small group room | Small room for assistance with individuals and groups up to 4 | 9 | RES02 (Small group room)
SEN01 | SEN resource base | Small room for assistance with individuals and groups with SEN | 16 | SEN01 (SEN resource base)
SEN11 | SEN therapy/ MI room | Room for physio- and other therapy and medical inspections | 12 | SEN11 (SEN therapy and MI r...
STN01 | Personal storage (cloakrooms) | Coat hooks and shelving for bags off circulation areas for pupils | As SoA | STN01 (Personal storage (cl...
STN02 | Personal storage (lockers) | Lockers off circulation areas for pupils | As SoA | STN02 (Personal storage (lo...
STT05 | DT light practical store (off room) | Store room for light practical resources or work in progress | 5 | STT05 (DT light practical s...
STT13 | General teaching/ IT store (off corridor) | Store room for general teaching or ICT resources | 5 | STT13 (General teaching and...

## ADM02 (Interview room)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Interview room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | ADM02
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Room off reception area for meetings with visitors without the need to access the main school
|  | Typical Area |  |  | typical area for group described | 6m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Interviews, some of which will be in private, with parents and visitors. Small group meetings for both staff and parents.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 4
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | Optional
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the space required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 6 |  | 6
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided Contractor to specify if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | Type D1.1 |  | Note 1
|  | Description |  |  |  | General, no vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997 | N/A
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A2.40/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Low
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 40 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R08 |  | R08
|  | Maximum reverberation time |  |  | seconds | <=0.8 |  | <=0.8
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Visitors Chair (with arms)/Admin |  | CHA302 |  | Gp3 |  | 4
|  | Meeting table, Admin |  | TAB505 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## ADM05 (General office (1 re...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | General office (1 recep desk) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | ADM05
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Main office for administrative staff, with reception desk for visitors, off entrance/ reception area
|  | Typical Area |  |  | typical area for group described | 41m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Welcoming visitors, administrative support to staff and welfare support to pupils .
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 10
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the space required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | As SoA |  | As SoA
|  | minimum ceiling height |  |  |  | 2700 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided Contractor to specify if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1a |  | Type L1.1a |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Required |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None [, unless a long way from tea making facilities.]
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Means to keep sensitive documents securely
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA001 |  | Gp2 |  | 6
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 2
|  | Operators chair (with arms)/Admin |  | CHA303 |  | Gp3 |  | 9
|  | Screen (Desk mounted) |  | SCR003 |  | Gp3 |  | 5
|  | Pedestal unit/Admin |  | STO101 |  | Gp3 |  | 9
|  | Tall tambour unit/Admin |  | STO102 |  | Gp3 |  | 6
|  | Table, ICT/Admin |  | TAB503 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 3
|  | Photocopier |  | EQ227 |  | Gp3 |  | 1
|  | Paper Shredder |  | EQ228 |  | Gp3 |  | 1

## ADM08 (Reprographics room)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Reprographics room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | ADM08
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Room for reprographics and photocopying machines
|  | Typical Area |  |  | typical area for group described | 20m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administrative work. Collating, finishing, photocopying, printing, scanning. Storage of paper and printing resources.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 3
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the space required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 20 |  | 20
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided Contractor to specify if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F2c |  | Type F2c
|  | Description |  |  |  | Chemical resistant lino, resin, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 33 |  | Commercial 33
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2 |  | 0.2
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | N/A |  | N/A
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | N/A |  | N/A
|  | Water Resistance |  |  |  | Yes |  | Yes
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | Yes |  | Yes
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern |  | Suitable for heavy movable FF&E on castors
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V7 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | 10 (see note)
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided. 20 l/s per machine that is operated more than 30 minutes per hour or 10l/s/p whichever is greater
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA001 |  | Gp2 |  | 1
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
|  | Shelving (set of 3) |  | SHE100 |  | Gp2 |  | 2
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | ICT staff chair |  | CHA301 |  | Gp3 |  | 2
|  | Cupboard unit (2 doors) |  | CUP004 |  | Gp3 |  | 2
|  | Tall tambour unit/Admin |  | STO102 |  | Gp3 |  | 6
|  | Table, ICT/Admin |  | TAB501 |  | Gp3 |  | 2
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1
|  | Large Bin |  | BIN002 |  | Gp3 |  | 2
|  | Photocopier |  | EQ227 |  | Gp3 |  | 3

## ADM11 (Head s office)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Head's office |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | ADM11
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Office for head teacher
|  | Typical Area |  |  | typical area for group described | 16m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administrative tasks (including use of ICT), small group meetings and interviews with pupils, staff, visitors and parents. Privacy important.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 8
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the space required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 16 |  | 16
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided Contractor to specify if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Lockable, openable windows or vents to be provided. Window head height to be as close to ceiling as possible
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1 |  | Note 1
|  | Description |  |  |  | General, no vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | Type D1.1 |  | Note 1
|  | Description |  |  |  | General, no vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997 | N/A
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1a |  | Type L1.1a |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Required |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Means to keep sensitive documents securely
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
|  | Shelving (set of 3) |  | SHE100 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
|  | Coat hooks (6) |  | STO001
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Filing cabinet (2 dr)/Admin |  | CAB103 |  | Gp3 |  | 1
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 2
|  | Visitors Chair (with arms)/Admin |  | CHA302 |  | Gp3 |  | 2
|  | Executive chair (with arms)/Admin |  | CHA304 |  | Gp3 |  | 1
|  | Tall tambour unit/Admin |  | STO102 |  | Gp3 |  | 2
|  | Meeting table, Semi-circular/Admin |  | TAB500 |  | Gp3 |  | 1
|  | Table, ICT/Admin |  | TAB504 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## OFF01 (Small 1-person office)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Small 1-person office |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF01
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Office for one member off staff, with admin storage
|  | Typical Area |  |  | typical area for group described | 7m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administrative tasks (including use of ICT) and filing.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 1
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the space required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 7 |  | 7
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Shelving (set of 3) |  | SHE100 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Filing cabinet (4 dr)/Admin |  | CAB101 |  | Gp3 |  | 1
|  | ICT staff chair |  | CHA301 |  | Gp3 |  | 1
|  | Visitors Chair (with arms)/Admin |  | CHA302 |  | Gp3 |  | 2
|  | Pedestal unit/Admin |  | STO101 |  | Gp3 |  | 1
|  | Rectangular table |  | TAB06R |  | Gp3 |  | 1
|  | Table, ICT/Admin |  | TAB502 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## OFF12 (Medium 2-person office)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Medium 2-person office |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF12
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Office for two members of staff, with space for meetings
|  | Typical Area |  |  | typical area for group described | 9m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administrative tasks (including use of ICT) small group meetings and interviews.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 4
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the area preferred
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 9 |  | 9
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA001 |  | Gp2 |  | 1
Fitted Furniture
|  | Shelving (set of 3) |  | SHE100 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 1
|  | Visitors Chair (with arms)/Admin |  | CHA302 |  | Gp3 |  | 2
|  | Operators chair (with arms)/Admin |  | CHA303 |  | Gp3 |  | 1
|  | Meeting table, Semi-circular/Admin |  | TAB500 |  | Gp3 |  | 1
|  | Table, ICT/Admin |  | TAB502 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1
|  | Paper Shredder |  | EQ228 |  | Gp3 |  | 1

## OFF23 (Office (SENco))
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Office (SENco) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF23
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Office for SENco and team
|  | Typical Area |  |  | typical area for group described | 12m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administrative tasks (including use of ICT). One-to-one teaching. Record keeping. Small group meetings and interviews/ counselling.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 4
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Full disabled access required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 12 |  | 12
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Optional. CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A2.40/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Low
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 40 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R04 |  | R04
|  | Maximum reverberation time |  |  | seconds | N/A |  | <=0.4
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Means to secure sensitive documents
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA001 |  | Gp2 |  | 2
Fitted Furniture
No FF&E Listed of This Type
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Filing cabinet (3 dr)/Admin |  | CAB103 |  | Gp3 |  | 1
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 2
|  | ICT staff chair |  | CHA301 |  | Gp3 |  | 2
|  | Pedestal unit/Admin |  | STO101 |  | Gp3 |  | 2
|  | Table, ICT/Admin |  | TAB503 |  | Gp3 |  | 2
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## OFF32 (Staff room (social))
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Staff room (social) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF32
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Main space for any staff in school to meet and socialise
|  | Typical Area |  |  | typical area for group described | As SoAm2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Informal meeting and discussion during breaks. Limited ICT access. Receiving post/notices. Relaxing and taking refreshments.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | As SoA
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the area required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | As SoA |  | As SoA
|  | minimum ceiling height |  |  |  | 2700 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Optional CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1 |  | Type L1.1 |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Required |  | Required
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw, dim
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | Hot and cold handwash and drinking water, including sink, teapoint, and dishwasher
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible | Some FF&E proportional to the number of workstations, as defined in the SoA 'group size', as shown in sample FF&E layouts.
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA002 |  | Gp2 |  | 3
|  | SS single bowl sink (right hand drainer) |  | SIN004 |  | Gp2 |  | 1
|  | Worktop 600 deep |  | WKTL600 | to longest wall | Gp2 |  | CTS
Fitted Furniture
|  | Underbench 2 door cupboard |  | CUB005 | to fit worktop length | Gp2 |  | CTS
|  | Underbench 1 door cupboard |  | CUB009 | to fit worktop length | Gp2 |  | CTS
|  | Wall cupboard unit (2 doors) |  | CUP013 | to fit worktop length | Gp2 |  | CTS
|  | Coat hooks (12) |  | STO002 |  | Gp2 |  | 1
Fitted equipment
|  | Wall mounted water boiler |  | APP004 |  | Gp2 |  | 1
Fixed Furniture
|  | Pigeon Holes unit (with tray unit under) |  | STO03X |  | Gp2 |  | 1
Fixed Equipment
|  | Dishwasher |  | APP001X |  | Gp3 |  | 1
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Large Bin |  | BIN002 |  | Gp3 |  | 1
|  | Practical stool |  | CHA024 | As SoA max group size x 0.12 | Gp3 |  | CTS
|  | Upholstered easy chair |  | CHA200 | As SoA max group size x 0.8 | Gp3 |  | CTS
|  | Screen |  | SCR001 |  | Gp3 |  | 4
|  | Adjustable table |  | TAB004 |  | Gp3 |  | 4
|  | Classroom chair |  | CHA005 | As SoA max group size x 0.3 | Gp3 |  | CTS
|  | Rectangular table |  | TAB006 | As SoA max group size x 0.1 | Gp3 |  | CTS
|  | Table, Coffee |  | TAB600 | As SoA max group size x 0.1 | Gp3 |  | CTS
|  | Table, Coffee (round) |  | TAB601 | As SoA max group size x 0.1 | Gp3 |  | CTS
Loose Equipment
|  | Microwave |  | APP001 |  | Gp3 |  | 1
|  | Refrigerator |  | APP002 |  | Gp3 |  | 1

## OFF33 (Staff work room)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Staff work room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF33
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Space for staff in [school or suite] to work and meet
|  | Typical Area |  |  | typical area for group described | SoAm2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Lesson preparation and research mainly using ICT with a hot desk arrangement. Marking and recording pupils work. Storage of some of staffs personal and teaching resources. Team meeting and discussions.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | As SoA
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the area required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | As SoA |  | As SoA
|  | minimum ceiling height |  |  |  | 2700 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A1.45/65 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 45 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 65 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R10 |  | R10
|  | Maximum reverberation time |  |  | seconds | <=1.0 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible | Some FF&E proportional to the number of workstations, as defined in the SoA 'group size', as shown in sample FF&E layouts.
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA002 |  | Gp2 |  | 2
|  | Fitted Worktop |  | WKTL600 | to 1 wall | Gp2 |  | CTS
Fitted Furniture
|  | Shelving (set of 3) |  | SHE100 |  | Gp2 |  | 3
|  | Coat hooks (6) |  | STO001 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 2
|  | ICT staff chair |  | CHA301 | As SoA max group size | Gp3 |  | CTS
|  | Pedestal unit/Admin |  | STO101 | As SoA max group size | Gp3 |  | CTS
|  | Table, ICT/Admin |  | TAB503 | As SoA max group size /2 | Gp3 |  | CTS
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## OFF41 (Conference and meeti...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Conference/ meeting room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | OFF41
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Conference room for meetings of staff, governors and other adults
|  | Typical Area |  |  | typical area for group described | 20m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Meeting room for staff with internal and external visitors etc. Privacy important. Small scale presentations using ICT.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 12
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | zone B
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | Optional
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access into the area required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 20 |  | 20
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above)
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A2.40/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Low
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 40 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R08 |  | R08
|  | Maximum reverberation time |  |  | seconds | <=0.8 |  | <=0.8
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Visitors Chair (with arms)/Admin |  | CHA302 |  | Gp3 |  | 12
|  | Meeting table, Semi-circular/Admin |  | TAB500 |  | Gp3 |  | 2
|  | Meeting table/Admin |  | TAB505 |  | Gp3 |  | 3
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## RES02 (Small group room)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Small group room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | RES02
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Small room for assistance with individuals and groups up to 4
|  | Typical Area |  |  | typical area for group described | 9m |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Individual/small group learning support. One to one counselling, privacy required.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | 4 | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 1
|  |  |  | Area Guidelines Category |  | Learning resources
|  |  |  | Area Guidelines Zone |  | Zone B
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Full disabled access required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 9 |  | 8.5
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above)
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Type D1.1v
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30 |  | 30
|  | Door leaf width |  |  | mm | 926 |  | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825 |  | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000 |  | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5 |  | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3 |  | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30 |  | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes |  | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No |  | No
|  | Vision panels |  |  | min height and width as FOS | Yes |  | Yes
|  | Ironmongery hardware: | Closer |  |  | No |  | No
|  |  | Cylinder/ lock |  |  | Yes |  | Yes
|  |  | Lever handle |  |  | Yes |  | Yes
|  |  | Vertical pull handle |  |  | No |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V1 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | 1000
|  |  |  | for natural ventilation | parts per million (ppm) | 1500
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | 1500
|  |  |  | for natural ventilation | parts per million (ppm) | 2000
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A3.35/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Average
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Medium
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 35 |  | 40
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R08.1 |  | R08.1
|  | Maximum reverberation time |  |  | seconds | <=0.8 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Whiteboard |  | BOW01 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Fixed Equipment
No FF&E Listed of This Type
Loose Furniture
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1
|  | Classroom chair |  | CHA002 |  | Gp3 |  | 4
|  | ICT Teachers chair |  | CHA301 |  | Gp3 |  | 1
|  | Adjustable table |  | TAB001 |  | Gp3 |  | 1
|  | Rectangular table |  | TAB03R |  | Gp3 |  | 1
Loose Equipment
No FF&E Listed of This Type

## SEN01 (SEN resource base)
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | SEN resource base |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | SEN01
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Small room for assistance with individuals and groups with SEN
|  | Typical Area |  |  | typical area for group described | 16m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Individual therapy and counselling. Individual/small group learning support. Staff meetings.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | 7 | / | 7
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 3
|  |  |  | Area Guidelines Category |  | Learning resources
|  |  |  | Area Guidelines Zone |  | Zone C
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Full disabled access required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 16 |  | 16
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Optional CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above)
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | Type D1.1v |  | Note 1
|  | Description |  |  |  | General, with vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997 | 35
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | Yes
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V1 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | 1000
|  |  |  | for natural ventilation | parts per million (ppm) | 1500
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | 1500
|  |  |  | for natural ventilation | parts per million (ppm) | 2000
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A2.40/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Low
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 40 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R08.1 |  | R08.1
|  | Maximum reverberation time |  |  | seconds | <=0.8 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA001 |  | Gp2 |  | 1
Fitted Furniture
|  | Whiteboard |  | BOAW01 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Side filing cabinet (2 dr) |  | CAB104 |  | Gp3 |  | 1
|  | Classroom chair |  | CHA001 |  | Gp3 |  | 4
|  | ICT staff chair |  | CHA101 |  | Gp3 |  | 1
|  | Pedestal unit |  | STO101 |  | Gp3 |  | 1
|  | Rectangular table |  | TAB006 |  | Gp3 |  | 1
|  | Semi circular table |  | TAB007 |  | Gp3 |  | 1
|  | 60 Tray unit (2 doors) |  | TRA004 |  | Gp3 |  | 1
Loose Equipment
No FF&E Listed of This Type

## SEN11 (SEN therapy and MI r...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | SEN therapy/ MI room |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | SEN11
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Room for physio- and other therapy and medical inspections
|  | Typical Area |  |  | typical area for group described | 12m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Administering drug treatments to pupils. Medical inspection by external practitioners. Physio- or speech therapy for pupils with special needs.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | 2 | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | 2
|  |  |  | Area Guidelines Category |  | Staff and admin
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | Optional for multi-agency work
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Full disabled access required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 12 |  | 12
|  | minimum ceiling height |  |  |  | 2400 |  | 2400
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | As existing
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above)
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D1.1 |  | Note 1
|  | Description |  |  |  | General, no vision panel |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 30
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 5
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | Yes
|  |  | Vertical pull handle |  |  | No
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1 |  | Type F1
|  | Description |  |  |  | General carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 32 |  | Commercial 32
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W3n |  | Type W3n
|  | Description |  |  |  | Jointless |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L1.1b |  | Type L1.1b |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Preferred |  | Preferred
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | 50% |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | 80% |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | 0.3
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 450 |  | 450
|  | Minimum ceiling luminance |  |  |  | 100 |  | 100
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | 150 |  | 150
|  | Max. CIBSE limiting glare index |  |  |  | 19 |  | 19
|  | Modelling Index |  |  |  | 0.3 to 0.5 |  | 0.3 to 0.5
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.6 |  | 0.6
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | d, occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T5 |  | Type T5 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 20 |  | 20
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | 18 |  | 18
|  | Maximum maintained air temperature (oC) |  |  |  | 26 |  | 26
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | 40 |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | 6 |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | 4 |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | 120
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | 5
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | 200 |  | 200
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | 15 |  | 15
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V6 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | A2.40/60 |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High | Low
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High | Low
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe) | 40 |  | 45
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w | 60 |  | 65
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A | 33 |  | 30
Or:
|  | Minimum composite Rw (dB) of corridor** wall and glazing without ventilators |  |  |  | 40 |  | 35
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable | 32 |  | 32
|  | Reverberation |  |  |  | R08.1 |  | R08.1
|  | Maximum reverberation time |  |  | seconds | <=0.8 |  | <=1.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a) | A means of increasing the air velocity during the summer shall be provided.
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets as FOS, within dado trunking on 2 walls where appropriate, plus cleaners' SSSO at low level
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | Cold, with hot and cold handwash
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Noticeboard |  | BOA002 |  | Gp2 |  | 1
|  | Curtian tracking |  | CUR001 | to contain bed | Gp2 |  | CTS
|  | Curtains |  | CUR002 | to contain bed | Gp2 |  | CTS
|  | SS single bowl sink (left hand drainer) |  | SIN004 |  | Gp2 |  | 1
|  | Worktop 600 deep |  | WKTL600 | to part of 1 wall | Gp2 |  | CTS
Fitted Furniture
|  | Underbench 2 door cupboard |  | CUB005 |  | Gp2 |  | 1
|  | Wall cupboard unit (2 doors) |  | CUP013 |  | Gp2 |  | 1
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
|  | Clock (wall mounted) |  | CLO001X |  | Gp3 |  | 1
Loose Furniture
|  | Medical Bed |  | BED001 |  | Gp3 |  | 1
|  | Side filing unit (2 dr)/Admin |  | CAB104 |  | Gp3 |  | 1
|  | Upholstered easy chair |  | CHA200 |  | Gp3 |  | 1
|  | ICT staff chair |  | CHA301 |  | Gp3 |  | 1
|  | Pedestal unit/Admin |  | STO101 |  | Gp3 |  | 1
|  | Table, ICT/Admin |  | TAB503 |  | Gp3 |  | 1
Loose Equipment
|  | Small Bin |  | BIN001 |  | Gp3 |  | 1

## STN01 (Personal storage (cl...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Personal storage (cloakrooms) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | STN01
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Coat hooks and shelving for bags off circulation areas for pupils
|  | Typical Area |  |  | typical area for group described | As SoAm2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Storing pupils personal belongings (coats, bags, books, PE equipment etc).
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | N/A
|  |  |  | Area Guidelines Category |  | Storage (non-teaching)
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access to at least 25% of coat hooks required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Open plan
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | As SoA |  | As SoA
|  | minimum ceiling height |  |  |  | 2400 |  | 2200
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | 750
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | N/A
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | Contractor to specify if provided
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | N/A |  | Note 1
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1d |  | Type F1d
|  | Description |  |  |  | Durable carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 33 |  | Commercial 33
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L7.3 |  | Type L7.3 |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Not required |  | Not required
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | N/A |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | N/A |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | N/A
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 200 |  | 200
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Minimum ceiling luminance |  |  |  | N/A |  | N/A
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 25 |  | 25
|  | Modelling Index |  |  |  | N/A |  | N/A
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.4 |  | 0.4
|  | Min. colour rendering (Ra) |  |  |  | 60 |  | 60
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T9 |  | Type T9 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 5 |  | 5
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | N/A |  | N/A
|  | Maximum maintained air temperature (oC) |  |  |  | N/A |  | N/A
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | N/A |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | N/A |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | N/A |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | N/A
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | N/A
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | N/A |  | N/A
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | N/A |  | N/A
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V2b |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | N/A |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe)
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A
Or:
Minimum composite Rw (dB) of corridor** wall and glazing without ventilators
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable
|  | Reverberation |  |  |  | R15 |  | R15
|  | Maximum reverberation time |  |  | seconds | <=1.5 |  | <=2.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a)
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | None
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Allow enough space for safe access.
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | N/A |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Coat hooks (6) |  | STO001 |  | Gp2 |  | 1
|  | Coat hooks (12) |  | STO002 |  | Gp2 |  | 2
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
No FF&E Listed of This Type
Loose Furniture
No FF&E Listed of This Type
Loose Equipment
No FF&E Listed of This Type

## STN02 (Personal storage (lo...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | Personal storage (lockers) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | STN02
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Lockers off circulation areas for pupils
|  | Typical Area |  |  | typical area for group described | As SoAm2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Storing pupils personal belongings (coats, bags, books, PE equipment etc).
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | N/A
|  |  |  | Area Guidelines Category |  | Storage (non-teaching)
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access to at least 25% of lockers required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Open plan
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | As SoA |  | As SoA
|  | minimum ceiling height |  |  |  | 2400 |  | 2200
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | 750
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required unless for fire. CTS if provided
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | CTS | / | N/A
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above)
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | N/A |  | Note 1
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F1d |  | Type F1d
|  | Description |  |  |  | Durable carpet, lino, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 33 |  | Commercial 33
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2, 0.15 if carpet |  | 0.2, 0.15 if carpet
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | No |  | No
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | No |  | No
|  | Water Resistance |  |  |  | No |  | No
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L7.3 |  | Type L7.3 |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Not required |  | Not required
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | N/A |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | N/A |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | 0.3 |  | N/A
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 200 |  | 200
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 300 |  | 300
|  | Minimum ceiling luminance |  |  |  | N/A |  | N/A
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 25 |  | 25
|  | Modelling Index |  |  |  | N/A |  | N/A
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.4 |  | 0.4
|  | Min. colour rendering (Ra) |  |  |  | 60 |  | 60
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T9 |  | Type T9 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 5 |  | 5
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | N/A |  | N/A
|  | Maximum maintained air temperature (oC) |  |  |  | N/A |  | N/A
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | N/A |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | N/A |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | N/A |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | N/A
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | N/A
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | N/A |  | N/A
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | N/A |  | N/A
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V2b |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | N/A |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe)
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A
Or:
Minimum composite Rw (dB) of corridor** wall and glazing without ventilators
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable
|  | Reverberation |  |  |  | R15 |  | R15
|  | Maximum reverberation time |  |  | seconds | <=1.5 |  | <=2.0
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a)
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | None
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Allow enough space for safe access.
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | N/A |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Locker (single, 4 high) |  | LOC014X | As SoA | Gp2 |  | CTS
Fitted Furniture
No FF&E Listed of This Type
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
No FF&E Listed of This Type
Loose Furniture
No FF&E Listed of This Type
Loose Equipment
No FF&E Listed of This Type

## STT05 (DT light practical s...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | DT light practical store (off room) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | STT05
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Store room for light practical resources or work in progress
|  | Typical Area |  |  | typical area for group described | 5m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Storing teaching resources and materials relevant to the teaching space (eg. art or graphics) and/or work in progress.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | N/A
|  |  |  | Area Guidelines Category |  | Storage (teaching)
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access not required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 5 |  | 5
|  | minimum ceiling height |  |  |  | 2400 |  | 2200
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | 1.5
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | N/A | / | N/A
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | N/A
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D6 |  | Note 1
|  | Description |  |  |  | Store room |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 0
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 3
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | No
|  |  | Vertical pull handle |  |  | Pull face
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F2 |  | Type F2
|  | Description |  |  |  | Light practical lino, resin, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 33 |  | Commercial 33
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2 |  | 0.2
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | N/A |  | N/A
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | N/A |  | N/A
|  | Water Resistance |  |  |  | Yes |  | Yes
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L7.2c |  | Type L7.2c |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Not required |  | Not required
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | N/A |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | N/A |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | N/A |  | N/A
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 100 |  | 100
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 150 |  | 150
|  | Minimum ceiling luminance |  |  |  | N/A |  | N/A
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 24 |  | 24
|  | Modelling Index |  |  |  | N/A |  | N/A
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.4 |  | 0.4
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | N/A |  | N/A | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level)
Maximum maintained air temperature (oC)
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met
2. maximum daily weighted exceedence
3. Upper limit temperature: maximum ΔT
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes
Maximum hours outside heating season when air temperature in the space is above 25oC (oC)
Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC)
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V2b |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | N/A |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe)
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A
Or:
Minimum composite Rw (dB) of corridor** wall and glazing without ventilators
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable
|  | Reverberation |  |  |  | N/A |  | N/A
|  | Maximum reverberation time |  |  | seconds
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a)
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | None
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Fire Containment.
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Stockroom shelving (set of 5) |  | SHE010 | to 2 walls | Gp2 |  | CTS
|  | Stockroom shelving (set of 5) |  | SHE020 | to 1 wall | Gp2 |  | CTS
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
No FF&E Listed of This Type
Loose Furniture
No FF&E Listed of This Type
Loose Equipment
No FF&E Listed of This Type

## STT13 (General teaching and...
AREA DATA SHEETS |  |  |  |  | notes & information for client |  | Area data for: |  |  |  |  | compliance checks
for spaces in: |  |  |  | name of generic space type |  |  | General teaching/ IT store (off corridor) |  | Contractor's Initial Proposal |  |  | Contractor's Proposal (incl school preferences) |  |  | Independent Certifier
ALL SUITES |  |  |  | reference code for generic space type |  |  | STT13
Key Data | [8 empty] | NOTE: Enter value only if different from default value, supporting information must be provided where variations are proposed.
|  | reference code |  | name of individual space | Contractor to amend in individual space-specific ADS | Generic
|  |  |  | ref code for individual space | Contractor to amend to code in SoA by Suite | Generic
1. Function
|  | Summary description |  |  | brief description of space | Store room for general teaching or ICT resources
|  | Typical Area |  |  | typical area for group described | 5m2 |  |  | list any activities not accommodated (separate each individual activity with a full stop, make sure each is written exactly as it is in the list provided)
|  | Activities description | Range of activities or uses to be accommodated |  | This text box describes the activities that should be able to take place in the space, which in turn will influence the choice of F&E and many of the requirements below, including the area. | Storing teaching resources including books, files and digital equipment.
|  |  |  | Maximum group size/ Net capacity workplaces | maximum (not average) teaching group | N/A | / | N/A
|  |  |  | maximum no.of staff | number of staff or adults over and above pupils | N/A
|  |  |  | Area Guidelines Category |  | Storage (teaching)
|  |  |  | Area Guidelines Zone |  | N/A
|  |  |  | Net capacity category |  | General
identify if available for community use during or after school day
|  | Community use |  | Third Party Use | community use during or outside core school day | None
FM issues
|  | Availability Priority Category |  |  |  | N/A |  |  |  | identify relevant spaces |  |  | identify relevant spaces
|  | Consequential Unavailability |  |  |  | N/A |  |  | N/A |  |  | N/A
Location and Space
| 2. Location and access | [8 empty] | actual location |  |  | actual location
|  | Location |  |  | school to identify where this space should be located | As SoA
|  | Access requirements |  |  | disabled access options | Disabled access not required
| 3. Organisation | [8 empty] | actual enclosure/ adjacency |  |  | actual enclosure/ adjacency
|  | Enclosure requirements |  |  | enclosed/ semi-enclosed/ open plan | Enclosed
|  | Adjacency requirements |  |  |  | As SSDB
| 4. Space |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual area/dims |  | note ref. | actual area/dims |  | note ref.
|  | Minimum area (m2) |  |  | based on teaching group size above | 5 |  | 5
|  | minimum ceiling height |  |  |  | 2400 |  | 2200
|  | Space depth (mm) |  | where required | between internal faces of external and internal walls | N/A
Fabric and environment
| 5. External door(s) |  |  | if required or preferred | i.e. direct access via external door | Not Required
| 6. Windows and internal doorsets |  |  |  |  | If new / remodel |  | If refurb / redec'n | actual dimension |  |  | actual dimension
|  | Window sill height (mm) |  |  | Contractor to specify (CTS) | N/A | / | N/A
description of window solution
|  | Specific external door or window requirements | ironmongery, access, locks, integral or external blinds (for blinds see FF&E below) |  | (requirement for external door identified in Access to outdoors above) | N/A
[6 empty] | If new / remodel |  | If refurb / redec'n | description of entrance doorset solution
|  | Doorset from circulation |  | including atria | see tech annexe doorsets | Type D6 |  | Note 1
|  | Description |  |  |  | Store room |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: corridor or non-teaching area |  |  | Rw (db) to BS EN ISO717-1:1997 | 0
|  | Door leaf width |  |  | mm | 926
|  | Minimum clear opening width |  |  | effective clear width in mm | 825
|  | Minimum clear opening height |  |  | effective clear height in mm | 2000
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000 | 3
|  | Minimum mechanical strength |  |  | BS EN1192:2000 | 3
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001 | 30
|  | Minimum security rating |  |  | security rating defined in LSP 1175 | Yes
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000 | No
|  | Vision panels |  |  | min height and width as FOS | No
|  | Ironmongery hardware: | Closer |  |  | No
|  |  | Cylinder/ lock |  |  | Yes
|  |  | Lever handle |  |  | No
|  |  | Vertical pull handle |  |  | Pull face
description of interlinking doorset solution
|  | Doorset to adjacent space of similar type |  |  | see tech annexe doorsets | N/A |  | N/A
|  | Description |  |  |  | No internal door required |  |  | value |  | note ref. | value |  | note ref.
|  | Acoustic airborne sound insulation rating for door into space from: teaching space (eg. of same type) |  |  | Rw (db) to BS EN ISO717-1:1997
|  | Door leaf width |  |  | mm
|  | Minimum clear opening width |  |  | effective clear width in mm
|  | Minimum clear opening height |  |  | effective clear height in mm
|  | Minimum mechanical durability |  |  | Class defined in BS EN12400:2000
|  | Minimum mechanical strength |  |  | BS EN1192:2000
|  | Minimum fire and smoke resistance (value of "##") |  |  | in FD##s BS476-22 or E##Sa BS EN1643-3:2001
|  | Minimum security rating |  |  | security rating defined in LSP 1175
|  | Minimum hygrothermal performance |  |  | class defined in BS EN1192:2000 and BS EN1294:2000
|  | Vision panels |  |  | min height and width as FOS
|  | Ironmongery hardware: | Closer
Cylinder/ lock
Lever handle
Vertical pull handle
specific doorset requirements met and additions
Specific doorset requirements
| 7. Finishes | [7 empty] | description of floor finish solution
|  | Floor finish |  |  |  | Type F2 |  | Type F2
|  | Description |  |  |  | Light practical lino, resin, rubber or vinyl |  |  | value |  | note ref. | value |  | note ref.
|  | BS EN 14041 essential characteristics |  |  |  | Yes |  | Yes
|  | BS EN 685 durability classification |  |  | European Flooring Use classification | Commercial 33 |  | Commercial 33
|  | BS EN 14904 Sports floor elasticity |  |  | Area elastic (A3) or point elastic (P3) | N/A |  | N/A
|  | Minimum reflectance |  |  | O.3 for all habitable rooms | 0.2 |  | 0.2
|  | Minimum Required Life (years) |  |  |  | 10 |  | 10
|  | Slip Resistance |  |  | (Ramp test rating, or R value) | N/A |  | N/A
|  | Slip Resistance Value (SRV) |  |  | and surface roughness | N/A |  | N/A
|  | Water Resistance |  |  |  | Yes |  | Yes
|  | Fire Performance |  |  |  | Yes |  | Yes
|  | Hygiene Performance |  |  |  | Moderate |  | Moderate
|  | BS EN14041 Electrostatic rating |  |  |  | Yes |  | Yes
|  | Chemical Resistance |  |  |  | No |  | No
|  | Heat Resistance |  |  |  | No |  | No
description of ceiling/ soffit finish solution
|  | Ceiling finish |  | or soffit finish | see technical annexe - ceiling finish | Type C1 |  | Note 1
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  | O.7 for all habitable rooms | 0.7
|  | Hygrothermal performance |  |  | generally as wall finish below | Normal
description of wall finish solution
|  | Wall finish |  |  | see technical annexe - wall finish | Type W1n |  | Type W1n
|  | Description |  |  |  | General |  |  | value |  | note ref. | value |  | note ref.
|  | Minimum reflectance |  |  |  | 0.5 |  | 0.5
|  | Impervious |  |  |  | N/A |  | N/A
|  | Jointless |  |  |  | N/A |  | N/A
|  | Smooth |  |  |  | Yes |  | Yes
|  | Hygrothermal performance |  |  |  | Normal |  | Normal
|  | Acoustic wall finish and absorbent panels |  |  |  |  | N/A
specific finishes requirements met and additions
|  | Specific finishes requirements |  | incl part-covering, colour or pattern
| 8. Environmental requirements |  |  |  |  | If new build |  | If refurbishment | identify if daylight provided |  |  | identify if daylight provided
|  | Daylight and lighting requirements |  |  | see technical annexe lighting | Type L7.2c |  | Type L7.2c |  |  | Yes/ No |  |  | Yes/ No
|  | Daylighting | [6 empty] | lighting sytem solution
|  | Direct daylighting requirement |  |  | required, preferred or not required | Not required |  | Not required
[9 empty] | value |  | note ref. | value |  | note ref.
|  | For new build: Daylight Autonomy |  | Required in 80% of spaces where daylight required (above) | Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | N/A |  | N/A
|  | Usable daylight Index, UDI-a |  |  | UDI-a to lie between 100 lux and 2000 lux for percentage of core hours | N/A |  | N/A
|  | For refurbishment: | Minimum uniformity of daylight |  | (under diffuse sky) where daylight provided | N/A |  | N/A
|  | Lighting system | [6 empty] | value |  | note ref. | value |  | note ref.
|  | Minimum horizontal/ task illuminance (lux) |  |  | maintained average | 100 |  | 100
|  | Maximum horizontal illuminance (lux) |  |  | maintained average | 150 |  | 150
|  | Minimum ceiling luminance |  |  |  | N/A |  | N/A
|  | Minimum cylindrical illuminance (lux) |  |  | at head height in teaching and learning spaces | N/A |  | N/A
|  | Max. CIBSE limiting glare index |  |  |  | 24 |  | 24
|  | Modelling Index |  |  |  | N/A |  | N/A
|  | Minimum uniformity of artificial lighting |  |  | at task position | 0.4 |  | 0.4
|  | Min. colour rendering (Ra) |  |  |  | 80 |  | 80
|  | Maximum lighting energy units (W/m2.100 lux) |  |  | Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L |  |  | (excluding track-mounted and emergency lighting) or higher if Part L changes in 2013. Contractor to Specify using suggested figures in technical annexe |  | Contractor to specify (CTS)
|  | Lighting Energy Numerical Index (LENI) |  |  | Contractor to specify (CTS) in new build (kWh/m2) | CTS |  | N/A
|  | Lighting controls |  |  | d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux | occ, sw
[9 empty] | identify any emergency lighting |  |  | identify any emergency lighting
|  | Emergency lighting |  |  | If community use or high risk areas | No
specific lighting requirements met and additions
|  | Specific lighting requirements | over and above those already required |  | notes, including specialist and task lighting (all occupied spaces shall allow for data screens to be used in a variety of positions without glare)
|  | Temperature and thermal comfort |  |  | see technical annexe - temperature T | Type T9 |  | Type T9 | value |  | note ref. | value |  | note ref.
|  | Normal maintained air temperature (1m above floor level at centre of room) (oC) |  |  | to be achieved by heating system in less than 20 minutes after closing any external doors | 5 |  | 5
|  | Type of ventilation |  |  | Contractor to specify (CTS): nat vent, mech vent or hybrid |  | Contractor to specify (CTS)
|  | Minimum maintained air temperature (oC) |  |  | provided by heating system in heating season, during maximum occupancy (1m above floor level) | N/A |  | N/A
|  | Maximum maintained air temperature (oC) |  |  |  | N/A |  | N/A
|  | CIBSE summertime overheating criteria: | [6 empty] | value |  | note ref. | value |  | note ref.
|  | 1. Maximum hours of exceedence |  |  | For new build only. 2 out of 3 of the CIBSE summertime overheating criteria must be met | N/A |  | N/A
|  | 2. maximum daily weighted exceedence |  |  |  | N/A |  | N/A
|  | 3. Upper limit temperature: maximum ΔT |  |  |  | N/A |  | N/A
|  | Maximum hours when air temperature in the space is above 28oC |  |  | In refurbishment and naturally ventilated spaces only | N/A |  | N/A
|  | Maximum difference between internal air temperature and external air temperature - oC |  |  | In refurbishment, when external temperature > 200C, when the spaces are occupied for more than 30 minutes | N/A |  | N/A
|  | Maximum hours outside heating season when air temperature in the space is above 25oC (oC) |  |  |  | N/A |  | N/A
|  | Minimum air temperature of air delivered at 1.4m above floor level in occupied zone (oC) |  |  |  | N/A |  | N/A
|  | Ventilation |  |  | see technical annexe - ventilation V | Type V2b |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Operational target for maximum average daily concentration of carbon dioxide (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day (ppm) |  | for mechanical ventilation | parts per million (ppm) | N/A
|  |  |  | for natural ventilation | parts per million (ppm) | N/A
|  | Minimum rate of ventilation when occupied |  |  | litres per second per person | N/A
|  | Maximum winter time cold air inlet velocity (m/s) |  |  | meters per second during occupation | 0.3
|  | Minimum capability rate of ventilation |  |  | in air changes per hour (ach) or litres per second per person (l/s/p) | N/A
|  | Acoustics |  |  | see technical annexe - acoustics A | N/A |  | Note 1 | value |  | note ref. | value |  | note ref.
|  | Room classification (for airbourne sound insulation) |  | Activity noise level | (Source room) Low/Average/High/Very High
|  |  |  | Noise tolerance | (Receiving room) Low/Medium/High
|  | Minimum Dw (dB) (between spaces of same type) |  |  | Contractor to specify (CTS) with reference to Acoustic Performance Standards for PSBP |  | Contractor to specify (CTS)
|  | Maximum indoor ambient noise level for ventilation to achieve 1500ppm Carbon Dioxide concentration |  |  | and for Nat Vent when nat vent paths are shut - see note 4 (tech annexe)
|  | Maximum impact sound pressure from above |  |  | sound pressure level L’w
Either:
|  | Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators |  |  | Contractor to identify which measure is being used and mark other as N/A
Or:
Minimum composite Rw (dB) of corridor** wall and glazing without ventilators
|  | Minimum Dn,e,w – 10logN dB for ventilators in walls |  |  | Dn,e,w – 10logN3 (dB) where applicable
|  | Reverberation |  |  |  | N/A |  | N/A
|  | Maximum reverberation time |  |  | seconds
specific environmental requirements met and additions
|  | Specific environmental requirements | (extraction units and fume cupboards covered under fittings, dim out covered under lighting) |  | requirements not covered in environmental headings above, including special exhaust ventilation, surface temp of heat emitters, minimum STI in open plan areas and intermittent ventilation (as Part L Table 6.1a)
| 9. Building services | [7 empty] | description of building services solutions
|  | Gas supply | As described |  |  | None
|  | Specific electrical services requirements | Including specialist power |  |  | Power sockets for recharging laptops where appropriate
|  | Specific wet services requirements | (water supply, drainage, sanitary ware and fixtures) |  |  | None
|  | Power sockets | [6 empty] | value |  | note ref. | value |  | note ref.
|  |  |  | Trunking at dado level |  | CTS
|  |  |  | Double Power Socket Total |  | CTS
|  |  |  | Single Power Socket Total |  | CTS
|  |  |  | Additional Power (Double Socket) |  | CTS
|  |  |  | Cleaner's Power (single socket) |  | CTS
Communication and ICT infrastructure
|  |  | Voice over Internet Protocol (VoIP) |  | Telephone system using data sockets | CTS
|  |  | Wifi AP Data Point |  |  | CTS
|  |  | Data Points Total |  | As specified in FOS | CTS
|  |  | Additional Data |  |  | CTS
|  |  | TV Signal point - IPTV |  | Central controller or receiver box | CTS
|  |  | Projector AV faceplate |  |  | CTS
|  |  | PA and alarms |  |  | CTS
| 10. Safety and security | [7 empty] | specific safety and security requirements met and additions
|  | Specific requirements |  |  | school to add additional requirements if necessary, including space between F&E | Fire Containment.
identify if sprinkers provided
|  | Sprinklers, where supplied |  |  |  | Contractor to Specify
11. Fittings, furniture and equipment
| Signage | [7 empty] | specific signage requirements met and additions
|  | Specific signage requirements |  |  | Not including doorset signage (covered below)
|  | Nameplate |  | at entry to space | Description on or adjacent to entrance or door | Add here text to be included on sign |  |  |  |  | Yes/ No |  |  | Yes/ No
identify any fire fighting equipment provided
|  | Fire fighting equipment | including fire extinguisher and holder |  | Contractor to specify particular appliances where provided | N/A
identify any first aid equipment provided
|  | First aid equipment |  |  |  | N/A
| Curtains and blinds | [7 empty] | specific curtain and blind requirements met and additions
|  | Specific curtain and blinds requirements |  |  | To internal and external windows and doors only | Contractor to specify if provided
ICT equipment |  |  |  |  | Contractor to Specify (CTS) ICT below, based on ICT Solution Summary and discussion with school
| Fixed ICT equipment |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
|  | Projector |  | Seperate |  | Gp3 |  | CTS
|  |  |  | Wall Mounted |  | Gp3 |  | CTS
|  |  |  | Ceiling Mounted |  | Gp3 |  | CTS
|  |  |  | Theatre |  | Gp3 |  | CTS
|  | Interactive Whiteboard |  |  |  | Gp3 |  | CTS
|  | Integrated IWB and projector |  |  |  | Gp3 |  | CTS
|  | Speakers |  |  |  | Gp3 |  | CTS
|  | Digital Display |  |  | (Plasma or LCD) | Gp3 |  | CTS
|  | Electric Screen |  |  |  | Gp3 |  | CTS
|  | Sound Field |  |  |  | Gp3 |  | CTS
Loose ICT equipment
|  | Projector - Mobile |  |  |  | Gp3 |  | CTS
|  | Teacher Laptop/Desktop |  |  |  | Gp3 |  | CTS
|  | Computer |  | Desktop |  | Gp3 |  | CTS
|  |  |  | Laptop |  | Gp3 |  | CTS
|  |  |  | Netbook |  | Gp3 |  | CTS
|  |  |  | Tablet |  | Gp3 |  | CTS
|  | Printer |  | Multi-function Device |  | Gp3 |  | CTS
|  |  |  | Workgroup |  | Gp3 |  | CTS
|  |  |  | Large Form Factor |  | Gp3 |  | CTS
|  | Laptop Trolley |  |  |  | Gp3 |  | CTS
|  | Networked Peripheral |  | Scanner |  | Gp3 |  | CTS
|  |  |  | VC Unit |  | Gp3 |  | CTS
|  |  |  | Visualiser |  | Gp3 |  | CTS
FF&E | [8 empty] | specific FF&E requirements met and additions
|  | Specific FF&E requirements | incl. extraction units and fume cupboards |  | Group 2 FF&E shall be provided to allow the activities listed above to be carried out safely, effectively and efficiently by the maximum number of pupils and/or staff, using FF&E with attributes similar to the indicative FF&E listed below. Contractor to reuse legacy items where possible
| Fittings |  |  |  |  | group |  | quantity | group |  | quantity | group |  | quantity | quantity
No FF&E Listed of This Type
Fitted Furniture
|  | Stockroom shelving (set of 5) |  | SHE020 | to 3 walls | Gp2 |  | CTS
Fitted equipment
No FF&E Listed of This Type
Fixed Furniture
No FF&E Listed of This Type
Fixed Equipment
No FF&E Listed of This Type
Loose Furniture
No FF&E Listed of This Type
Loose Equipment
No FF&E Listed of This Type

## Technical Annexes
Technical Annexe
Doorsets |  |  | N/A | Type D1.1 | Type D1.1v | Type DD1.1v | Type D1.1vs | Type D1.2v | Type D1.2vs | Type D1.2vh | Type D1.2vhs | Type D2v | Type D2vs | Type DD1.1v | Type DD1.1vp | Type DD2v | Type DD2vs | Type DD3v | Type D4.1 | Type D4.1s | Type D4.1n | Type D4.1ns | Type D4.2 | Type D4.2s | Type DD5v | Type DD5vs | Type D6 | Type D6h | Type D7 | Type D7v | Type D7vh | Type D8 | Type D8h | Type DD9
Areas, spaces that doorsets lead into |  |  |  | Head and senior staff offices | In mainstream schools: general teaching, light practical, libraries, small group rooms, most staff and admin spaces | Door between paired general teaching, light practical, small group rooms, or staff and admin spaces | Nursery playrooms and, in special schools: general teaching, light practical, libraries, small group rooms for predominantly ambulant pupils | Resistant materials and engineering and adjacent spaces of similar humidity | In special schools: general teaching, practical, libraries, small group rooms for predominantly non-ambulant pupils | In mainstream schools: food or catering rooms, food store, and kitchen preparation areas | In special schools: food or catering rooms, food store, and kitchen preparation areas | Any teaching and learning spaces designed for pupils with special hearing or communication needs (note 4), and in mainstream schools: music and performance spaces (including those likely to have amplified music) | In special schools: music and performance spaces (including those likely to have amplified music) | In mainstream schools, dining or social areas (double doors - not lobbied doors) | In special schools, dining or social areas (double doors - not lobbied doors) | In mainstream schools: multi-use and assembly halls, performance spaces (double doors - not lobbied doors) | In special schools: multi-use and assembly halls, performance spaces (double doors - not lobbied doors) | Sports halls, activity studios, gymnasia | Toilets (main entrance to toilet suites) and changing rooms for non-disabled | In special schools: toilets (main entrance to toilet suites) and changing rooms for predominantly ambulant pupils | Individual rooms for toilets for non-disabled (not including cubicle doors) | In nursery provision and special schools: toilets and hygiene rooms for predominantly ambulant pupils | Toilets and changing rooms for SEN and disabled | In special schools: hygiene rooms and changing rooms for disabled and non ambulant pupils | In mainstream schools: mineral purpose for circulation routes and securing areas | In special schools: general purpose for circulation routes and securing areas | Store rooms and cupboards containing materials for lightweight activities | Store rooms or cupboards or stores off food, kitchen preparation or toilet areas | Materials storage and preparation areas for heavy practical activities. | Materials storage and preparation areas for heavy practical activities. | Food technology food store from circulation and kitchen walk-in store rooms off kitchen preparation area | Chemical and other hazardous material stores, service ducts and plant rooms | Chemical and other hazardous material stores, service ducts and plant rooms accessed from humid areas such as kitchens | hall, sports hall, activity studio and gymnasium stores
Description |  |  | no internal door required | general, no vision panel | general, with vision panel | general, with vision panel | special general, with vision panel | strong, with vision panel | special strong, with vision panel | strong, with vision panel, humid areas | special strong, with vision panel, humid areas | acoustic, with vision panel | special acoustic, with vision panel | double general, with vision panels | special double general, with vision | double acoustic, with vision panel | special double acoustic, with vision | sports hall, with vision panels | suitable for wet areas | special suitable for wet areas | suitable for toilets | special suitable for toilets | suitable for wet areas and durable | Special suitable for wet areas | circulation, with vision panel | Special circulation, with vision panel | store room | store room in humid areas | fire-resistant, no vision panel | fire-resistant, with vision panel | fire-resistant, with vision panel, humid | fire-resistant cupboard or plant | fire-resistant cpd or plant, humid | hall store
Acoustic airborne sound insulation rating (Rw (db) to BS EN ISO717-1:1997) - for door into space from: | corridor or non-teaching area | Contactor to identify alternative depending on adjacent rooms |  | 30 | 30 | N/A | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 30 | 30 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| teaching space (e.g. of same type) |  |  | N/A | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Door leaf width |  |  |  | 926 | 926 | 926 | 926 | 926 | 1026 | 926 | 1026 | 926 | 1026 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 1026 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926
Minimum clear opening width of single leaf (double leaves) |  |  |  | 825 | 825 | 825 | 825 | 825 | 925 | 825 | 925 | 825 | 925 | 825 (1500) | 825 (1650) | 825 (1500) | 825 (1500) | 875 (1200) | 825 | 825 | 825 | 825 | 825 | 925 | 825 (1650) | 825 (1650) | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 (1650)
Minimum clear opening height |  |  |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 (see note)
Mechanical durability (Class defined in BS EN12400:2000) |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 5 | 5 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Mechanical strength (BS EN1192:2000) |  |  |  | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 4 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 3 | 4 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
Fire and smoke resistance (value of "##" in FD##s to BS476-22 or E##Sa to BS EN1643-3:2001), dependent on fire strategy |  | Contactor to identify alternative depending on fire strategy |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 | 0
Security (security rating defined in LSP 1175) |  |  |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Hygrothermal performance (class defined in BS EN1192:2000 and BS EN1294:2000) |  |  |  | no | no | no | no | no | no | yes | yes | no | no | no | no | no | no | no | yes | yes | yes | yes | yes | yes | no | no | no | yes | no | no | yes | no | yes | no
Vision panels (between 500mm and 1500m from floor, located towards leading edge with room for ironmongery) |  |  |  | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes, with safety glass | no | no | no | no | no | no | yes | yes | no | no | no | yes | yes | no | no | no
Closer |  |  |  | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | yes | yes | no | no | no | no | no | yes | yes | no
Electromagnetic hold open device |  |  |  | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no | yes | yes | no | no | no | no | no | no | no | no
Hinges |  |  |  | standard | standard | parliament | protected | standard | protected | standard | protected | standard | protected | standard | protected | standard | protected | standard | standard | protected | see note | protected | standard | protected | standard | protected | standard | standard | standard | standard | standard | standard | standard | standard
Cylinder/ lock |  |  |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | deadlock only | deadlock only | deadlock only | deadlock only | deadlock only | deadlock only | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lever handle |  |  |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | no | no | no | no | no | yes | yes | no | no | no | no | yes | yes | yes | no | no | no
Vertical pull handle |  |  |  | no | no | no | no | no | no | no | no | no | no | no | no | no | no | pull face | pull face | pull face | pull face | pull face | both faces | both faces | pull face | pull face | pull face | pull face | no | no | no | pull face | pull face | no
Staff-only access control system | to BS EN 50133-1 |  |  | no | no | no | yes | no | yes | no | yes | no | yes | no | yes | no | yes | no | no | yes | no | yes | no | yes | optional | yes | no | no | no | no | no | no | no | no
Door protection: kick plate height (mm) | if door not steel or timber with laminated finish |  |  | 200 | 200 | 200 | 200 | 200 | 450 | 200 | 200 | 200 | 200 | 200 | 450 | 200 | 450 | 200 | 200 | 450 | 200 | 450 | 450 | 450 | 200 | 450 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Notes | [5 empty] | Doors to open 180o | Ergonomic handle and access control system to be agreed with school |  | Ergonomic handle and access control system to be agreed with school |  | Ergonomic handle and access control system to be agreed with school |  | Ergonomic handle and access control system to be agreed with school | Plain meeting stiles | Plain meeting stiles | Plain meeting stiles | Plain meeting stiles. Ergonomic handle and access control system to be agreed with school | Plain meeting stiles. Must open out from hall space. All surfaces must be flush with no projecting frames or ironmongery |  | Ergonomic handle and access control system to be agreed with school | Door leaf shall open inwards but be openable outwards in an emergency | Access control system to be agreed with school. If door leaf opens inwards it shall be openable outwards in an emergency | Ergonomic handle | Ergonomic handle and access control system to be agreed with school |  | Ergonomic handle and access control system to be agreed with school | [5 empty] | Door should open outwards and be unlockable from inside the room. | Door should open outwards and be unlockable from inside the room. | Dimensions to suit equipment to be stored, particularly trampolines
Notes on suffixes (see relevant door set type table) |  |  |  | Suffix v denotes a vision panel or panels between 500mm and 1500mm above floor, and at least 250mm wide . |  |  | Suffix s denotes hinge protection and access control for special schools or nurseries. |  |  | Suffix h denotes a requirement for hygrothermal performance. |  |  | Suffix n denotes a deadlock only, with facility to open from outside in an emergency. |  |  | Suffix P denotes parliament hinges to allow doors to be opended 180o.
Floor Finishes - see also suffixes |  |  | N/A | Type F1 | Type F1p | Type F1.1 | Type F2sc | Type F2 | Type F2c | Type F2sh | Type F3 | Type F4 | Type F4hw | Type F5 | Type F6 | Type F2cdw | Type F1d | Type F2sch | Type F2sdw | Type F7 | Type F8
Area |  |  |  | in mainstream schools: general | mainstream primary classrooms | in special schools: general | science, art, cleaners store | electronics, graphics, stores, server room | wet textiles in art, chemical store, reprographics | food room, MI, medical treatment or nurses rooms | resistant materials workshops and prep, kiln room | drama studio, fitness/ multi-gym | multi-purpose hall | activity studio, dance studio, gymnasium | sports hall | dining area | atria and corridors | kitchen staff and stores | serveries | changing rooms, showers | kitchen
Description |  |  |  | general carpet, lino, rubber or vinyl | general carpet, lino, rubber or vinyl | impervious carpet, lino, rubber or vinyl | light practical non-slip lino, resin, rubber or vinyl | light practical lino, resin, rubber or vinyl | chemical resistant lino, resin, rubber or vinyl | light practical hygienic lino, resin, rubber or vinyl | heavy practical concrete, resin, rubber or vinyl | hall lino, rubber, timber, composition or vinyl | hygienic waterproof lino, rubber, timber or vinyl | semi-sprung timber floor | sports hall floor | durable waterproof lino, resin, rubber or vinyl | durable carpet, lino, rubber or vinyl | light practical non-slip hygienic lino, resin, rubber or vinyl | non-slip durable waterproof lino, resin, rubber or vinyl | wet area ceramic, resin, rubber or vinyl | heat resistant wet area ceramic, resin, rubber or vinyl
BS EN 14041 Essential characteristics |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes for rubber or vinyl | Yes for vinyl | Yes for vinyl | N/A | Yes for vinyl | Yes | Yes | Yes | Yes | Yes for vinyl | Yes for vinyl
BS EN 685 European Flooring Use classification (for durability) |  |  |  | Commercial 32 | Commercial 32 | Commercial 32 | Commercial 33 | Commercial 33 | Commercial 33 | Commercial 33 | Commercial 33 | Commercial 34 | Commercial 34 | N/A | N/A | Commercial 34 | Commercial 33 | Commercial 33 | Commercial 34 | Commercial 34 | Commercial 34
Area elastic (A3) or point elastic (P3) sports floor | to BS EN 14904: 2006 |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | A3 | P3 | N/A | N/A | N/A | N/A | N/A | N/A
Minimum reflectance |  |  |  | 0.2, 0.15 if carpet | 0.2, 0.15 if carpet | 0.2, 0.15 if carpet | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2, 0.15 if carpet | 0.2 | 0.2 | 0.2 | 0.2
Minimum Required Life (years) |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Slip Resistance (Ramp test rating, or R value) |  |  |  | No | No | No | R10 | N/A | N/A | R10 | R11 | No | No | No | Yes | No | No | R10 | R10 | Yes, see note | R11
Slip Resistance Value (SRV) and surface roughness |  |  |  | No | No | No | N/A | N/A | N/A | N/A | Minimum SRV 36 | No | No | No | N/A | No | No | SRV36 + 20 microns | SRV36 + 20 microns | Minimum SRV 36 | Minimum SRV 36
Water Resistance |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes
Fire Performance |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Hygiene Performance |  |  |  | Moderate | Moderate | High | Moderate | Moderate | Moderate | High | Moderate | Moderate | High | Moderate | Moderate | High | Moderate | High | High | High | High
Electrostatic |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | No
Chemical Resistance |  |  |  | No | No | No | Yes | No | Yes | No | Yes | No | No | No | No | No | No | Yes | No | Yes | Yes
Heat Resistance |  |  |  | No | No | No | No | No | No | No | Yes | No | No | No | No | No | No | No | No | No | Yes
Specific finishes requirements | Incl part-covering, colour or pattern |  |  |  | Carpet to part of area as shown on FF&E layout | Suitable for wheelchairs, readily cleanable and not hold smells, no transition strips | Suitable for heavy movable FF&E on castors |  | Suitable for heavy movable FF&E on castors | Suitable for heavy movable FF&E on castors | Suitable for heavy movable FF&E on castors |  | Suitable for movable bleacher seating |  | floor markings to be suitable for sports to be accommodated |  |  |  |  | Barefoot areas shall be 'barefoot slip resistance category B'
Notes on suffixes (see relevant floor type table) |  |  |  | Suffix s denotes a sub-type with an increased slip resistance requirement. |  |  | Suffix c denotes a sub-type with an increased chemical resistance requirement. |  |  | Suffix d denotes a sub-type with an increased durability requirement. |  |  | Suffix h denotes a sub-type with a high hygiene requirement. |  |  | Suffix w denotes a sub-type with a high hygiene and increased water resistance over other floors of that type. |  |  | Suffix p denotes a partial area of carpet denoted on the F&E layout (for instance for stories in infant classrooms).
All ceiling or soffit finishes |  |  | N/A | Type C1 | Type C2 | Type C3
Area |  |  |  | all areas not subject to humid/ wet conditions or high hygiene requirements | food room, kitchen preparation areas, kitchen staff and store rooms, toilets, changing rooms, plant rooms | showers
Description |  |  |  | general | humid areas | wet areas
Minimum reflectance |  |  |  | 0.7 | 0.7 | 0.7
Hygrothermal performance |  |  |  | normal | humid | wet
|  |  |  | F1n | F2n | F3h |  | F1ns | F2ns | F3 | F2h | F1h | F3w
All wall finishes |  |  | N/A | Type W1n | Type W2n | Type W3h | Type W4 | Type W1ns | Type W2ns | Type W3n | Type W2h | Type W1h | Type W3w
Area |  |  |  | all areas not subject to humid/ wet conditions or high hygiene requirements | science laboratories, science prep rooms | food room | all areas not requiring a smooth wall finish, such as DT workshops and DT prep rooms, corridors | halls and performance spaces, SEN resource and libraries, circulation | dining and sandwich areas | sports hall, sick bay, medical room | maintenance and cleaners stores, kitchen staff and store rooms, toilets, changing rooms, chemical stores | plant rooms | showers
Description |  |  |  | general | science | humid | rough | acoustic | dining | jointless | humid areas and toilets | plant | wet areas
Minimum reflectance |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Impervious - able to resist the penetration of water, solutions containing detergents, disinfectants and other liquids likely to be encountered in school buildings |  |  |  | N/A | yes | yes | N/A | N/A | yes | N/A | yes | N/A | yes
Jointless - without joints, or having joints that are sealed by methods which make the whole surface impervious and prevent the collection of dirt and bacteria |  |  |  | N/A | N/A | yes | N/A | N/A | N/A | N/A | N/A | N/A | yes
Smooth - no coarser than brush-applied matt emulsion paint on a flat plastered surface without projections, indents or holes part-way through the material |  |  |  | yes | yes | yes | N/A | yes | yes | yes | yes | yes | yes
Hygrothermal performance |  |  |  | normal | normal | humid | normal | normal | normal | normal | humid | humid | wet
Acoustic wall finish and absorbent panels to suit reverberation time required depending on ceiling acoustic treatment. |  | Contactor to identify if required |  | N/A | N/A | N/A | N/A | Contractor to identify | N/A | N/A | N/A | N/A | N/A
Notes on suffixes (see relevant floor type table) |  |  |  | Suffix n denotes normal hygrothermal performance requirement. |  |  | Suffix h denotes humid hygrothermal performance requirement. |  |  | Suffix w denotes wet hygrothermal performance requirement. |  |  | Suffix s denotes that an acoustic wall finish may be required, but this should be identified by the Contractor if used
Lighting Systems |  |  | N/A | Type L1.1 | Type L1.1a | Type L1.1b | Type L1.2 | Type L2.1 | Type L2.1e | Type L3 | Type L4 | Type L5 | Type L6 | Type L7.1 | Type L7.2 | Type L7.2s | Type L7.3 | Type L7.2c | Type L8
Area | Note: Solar gain and glare should be eliminated in all daylit spaces |  |  | Basic teaching except libraries and learning resource areas | Large learning resource areas, including libraries, and extensively used admin and staff areas, including head teachers office and general office | Small learning resource areas, such as small group rooms, ICT-rich resource areas and occasionally used admin and staff areas | Nursery spaces | Practical spaces where higher lighting level is needed (e.g. Art) | High risk practical areas - resistant materials workshops and preparation rooms | Performance spaces | Sports and Multi-purpose halls | Entrance, Reception, Dining and Social areas | Circulation | Kitchens | Toilets, hygiene rooms and changing rooms | In special schools - toilets, hygiene rooms and changing rooms | Plant rooms incl server room, lockers and cloaks, chemical store | Storage areas | dark room, control room, sensory rooms
Daylighting
Daylighting requirement | New build |  |  | required | required | preferred | required | required | required | required | required | required | preferred | preferred | preferred | preferred | not required | not required | none
| Refurbishment |  |  | required | preferred | preferred | required | required | required | preferred | preferred | preferred | preferred | preferred | preferred | preferred | not required | not required | none
Daylight Autonomy: Percentage of regularly used area that has an illuminance of 300 lux for half of core hours | New build | Required in 80% of spaces where daylight required (above). Contractor to add if relevant in refurbishment |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Refurbishment |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Usable daylight Index: UDI-a to lie between 100 lux and 2000 lux for percentage of core hours, UDI-a | New build |  |  | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Refurbishment |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Minimum uniformity of daylight (under diffuse sky) | Refurbishment | Where daylight provided (not required if DA and UDI specified) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A
Maximum number of core hours for which UDI-exceeded, UDI-e | Refurbishment |  |  | 20% | 20% | 20% | 20% | 20% | 20% | 10% | 10% | 20% | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Lighting System
Minimum average maintained horizontal/task illuminance - lux |  |  |  | 300 | 300 | 300 | 300 | 500 | 500 | 300 | 300 | 200 | 100 | 500 | 200 | 200 | 200 | 100 | 100
Maximum average maintained horizontal illuminance - lux |  |  |  | 450 | 450 | 450 | 450 | 750 | 750 | 450 | 450 | 300 | 150 | 750 | 300 | 300 | 300 | 150 | 150
Minimum ceiling luminance |  |  |  | 100 | 100 | 100 | 100 | 165 | 165 | 100 | 100 | 70 | 70 | N/A | 70 | 70 | N/A | N/A | N/A
Minimum cylindrical illuminance at head height - lux |  |  |  | 150 | N/A | 150 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Maximum CIBSE limiting glare index |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 25 | 22 | 22 | 22 | 25 | 24 | 25
Modelling Index |  |  |  | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | 0.3 to 0.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Minimum uniformity at task position of artificial lighting |  |  |  | 0.6 | 0.6 | 0.6 | 0.4 | 0.6 | 0.6 | N/A | 0.6 | 0.4 | 0.4 | 0.6 | 0.4 | 0.4 | N/A | N/A | 0.4
Minimum colour rendering (Ra) |  |  |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 60 | 80 | 80
Maximum lighting energy units W/m2.100 lux |  | Suggested figures: Contractor to specify |  | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 3.75 | 3.75 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Minimum initial efficacy - Luminaire lumens / circuit watt with allowance for control factors as in Approved Documents in support of Part L (Note: or higher if required by Part L changes in 2013) |  |  |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Lighting Energy Numerical Index (LENI) - kWh/m2 | New build | Contractor to specify |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Refurbishment |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Controls (d-daylight linking, sw - central manual switching, occ - occupancy, dim - dimming to 10 lux) |  |  |  | d, occ, sw, dim | d, occ, sw | d, occ, sw | d, occ, sw | d, occ, sw, dim | d, sw, dim | d, occ, sw, dim | d, occ, sw | d, occ, sw | d, occ, sw | sw | occ, sw | sw | sw | occ, sw | sw
Emergency lighting (required to ensure safe escape and evacuation where there is dangerous machinery or public access during evening) |  |  |  | no | no | no | no | no | yes | yes | yes | if fire exit | if fire exit | yes | no | no | no | no | yes
Notes: Control gear in all spaces to be High Frequency or Electronic with losses of not more than 0.5 Watts in standby mode until 2017 and 0 Watts thereafter. | [7 empty] | 300 lux as in classrooms can be used if a higher lighitng level can be achieved by task lighting or dimming if required. | 300 lux as in classrooms can be used if a higher lighitng level can be achieved by task lighting or dimming if required. |  | Default illuminance 300 lux, but option to switch to 500 lux for some sports useful, see LG5 | 300 lux available and limiting glare index of 19 to reception desk |  | High risk tasks for emergency lighting |  | Direct view of lamps from bed position to be avoided where applicable
Notes on suffixes (see relevant lighting table) |  |  |  | Suffix a denotes daylight preferred but not required in refurbishment |  |  | Suffix b denotes daylight preferred but not required in new build and refurbishment |  |  | Suffix c denotes daylight not required in new build and refurbishment |  |  | Suffix e denotes emergency lighting and no occupancy controls due to high risk
Temperature |  |  | N/A | Type T1 | Type T2 | Type T3 | Type T4 | Type T5 | Type T5a | Type T6 | Type T6a | Type T7 | Type T7a | Type T8 | Type T9
Areas, spaces | (note: values for refurbishment only in brackets) |  |  | Where young children or those with SEN or physical disabilities may be wet or partially clothed for a significant length of time | Where pupils or adults may be wet and partially clothed for a significant length of time, such as swimming pools | Special schools and resourced provision, where needs of pupils tend to be complex, including pupils with physical difficulties or profound and multiple learning difficulties. | Spaces with less than normal level of activity or clothing, including sick, isolation rooms, changing rooms; and gymnasia and dance and activity studios | Spaces with normal level of activity, teaching, study, exams, admin and staff areas, prep rooms | kitchen preparation areas | Spaces with higher than normal level of activity, such as sports halls not used for other purposes, or sleeping | Spaces with higher than normal level of activity, such as sports halls not used for other purposes, or sleeping | circulation spaces and store rooms normally occupied | Toilets | Server Rooms | Stores
Normal maintained air temperature (1m above floor level at centre of room) to be achieved by the heating system in less than 20 minutes after closing any external doors - oC |  |  |  | 25 | 23 | 23 | 21 | 20 | 20 | 17 | 17 | 18 | 18 | See note | 5
Minimum maintained air temperature provided by heating system in heating season (1m above floor level) - oC |  |  |  | 23 | 21 | 21 | 19 | 18 | 15 | 15 | 15 | 15 | 15 | See note | N/A
Maximum air temperature provided by heating system in heating season during maximum occupancy (1m above floor level) - oC |  |  |  | 30 | 28 | 25 | 26 | 26 | N/A | 23 | 23 | 21 | 21 | See note | N/A
CIBSE summertime overheating criteria:
1. Maximum hours of exceedence | New build | For new build 2 out of 3 of the CIBSE summertime overheating criteria must be met |  | 40 | 40 | 40 | 40 | 40 | N/A | 40 | 40 | 40 | N/A | N/A | N/A
2. maximum daily weighted exceedence | New build |  |  | 6 | 6 | 6 | 6 | 6 | N/A | 6 | 6 | 6 | N/A | N/A | N/A
3. Upper limit temperature: maximum ΔT | New build |  |  | 4 | 4 | 4 | 4 | 4 | N/A | 4 | 4 | 4 | N/A | N/A | N/A
Maximum hours when air temperature in the space is above 28oC for naturally ventilated buildings | Refurbishment | (refurbishment only) |  | 120 | 120 | 120 | 120 | 120 | (N/A) | 120 | 120 | (N/A) | (N/A) | (N/A) | (N/A)
Maximum difference between internal air temperature and external air temperature when external temperature > 200C, when the spaces are occupied for more than 30 minutes - oC |  | (refurbishment only) |  | 5 | 5 | 5 | 5 | 5 | N/A | 5 | 5 | N/A | N/A | N/A | N/A
maximum hours outside heating season when air temperature in the space is above 25oC for mechanically ventilated buildings |  |  |  | 200 | 200 | 200 | 200 | 200 | N/A | 200 | 200 | 200 | N/A | N/A | N/A
Minimum air temperature of air delivered at 1.4m above floor level in occupied zone |  |  |  | 20 | 18 | 18 | 16 | 15 | 12 | 12 | 12 | 12 | 12 | N/A | N/A
Notes: Air temperatures and velocities and radiant temperature asymmetry are inter-related. The figures here are minimum standards based on ASHRAE Standard 55 and a Percentage People Dissatisfied of 20%. |  | Design temperature should compensate for any rapidity of air movement leading to chilling by evaporation |  | In areas used for medical inspection, bathing and changing, the air speed in these environments should not exceed 0.1 m/s at 25°C. | And no more than 1oC above or below that of water temperature based in pool, subject to a maximum of 30oC (temperature based on maximum pool temperature of 29oC). | A means of increasing the air velocity during the summer shall be provided. | A means of increasing the air velocity during the summer shall be provided. | A means of increasing the air velocity during the summer shall be provided. | Workplace regulations apply | A means of increasing the air velocity during the summer shall be provided. | A means of increasing the air velocity during the summer shall be provided. Heating needs to operate at higher temperature during exams. | A means of increasing the air velocity in circulation areas during the summer shall be provided. |  | Minimum temperature in server room of 15oC Temperatures above server racks to be below 270C air temperature for legacy servers and below 330C or as specified with manufacturer for new equipment. | Minimum temperature in chemical stores is 10oC.
Notes on suffixes (see relevant temperature table) |  |  |  | Suffix a denotes an amendment to the standard
Ventilation |  |  | N/A | Type V3a | Type V3b | Type V6 | Type V7 | Type V1 | Type V1a | Type V1b | Type V2 | Type V2a | Type V2b | Type V2c | Type V2d | Type V3 | Type V4 | Type V5
Areas, spaces |  |  |  | Physiotherapy, medical and sick rooms | Kiln room, dark room, heat bay if in separate room | Staff and Admin offices | Reprographics | All occupied spaces used for education purposes | practical spaces other than science involving fumes (ceramics, wet textiles, food or dying) | science spaces involving fumes | Halls | Sports halls | Circulation, stores | Kitchens | Toilets and changing areas for non-disabled | Toilets, hygiene and changing rooms for SEN and disabled | Science Prep Room | Chemical store
Operational target for maximum average daily concentration of carbon dioxide/parts per million (ppm) | for mechanical ventilation |  |  | 1000 | N/A | N/A | N/A | 1000 | 1000 | 1000 | 1000 | 1000 | N/A | N/A | N/A | N/A | N/A | N/A
| for natural ventilation |  |  | 1500 | N/A | N/A | N/A | 1500 | 1500 | 1500 | 1500 | 1500 | N/A | N/A | N/A | N/A | N/A | N/A
Maximum carbon dioxide concentration not to be exceeded for more than 20 minutes each day | for mechanical ventilation |  |  | 1500 | N/A | N/A | N/A | 1500 | 1500 | 1500 | 1500 | 1500 | N/A | N/A | N/A | N/A | N/A | N/A
| for natural ventilation |  |  | 2000 | N/A | N/A | N/A | 2000 | 2000 | 2000 | 2000 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A
Minimum rate of ventilation when occupied (litres per second per person) |  | not measured |  | N/A | N/A | N/A | 10 (see note) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Maximum winter time cold air inlet velocity during occupation – m/s at 1m above floor (e.g. seated head level) |  |  |  | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.3 | N/A
Minimum capability rate of ventilation in air changes per hour (air changes per hour) |  |  |  | N/A | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 10 (see note) | 5 | 2
Notes (including Intermittent extract rate as Building Regulations AD F Table 6.1a). Air temperatures and velocities and radiant temperature asymmetry are inter-related. Minimum standards based on ASHRAE Standard 55 and a Percentage People Dissatisfied of 20% are recommended, See FOS. |  |  |  |  | extract required for kiln or specialist equipment to satisfy manufacturer's requirements |  | 20 l/s per machine that is operated more than 30 minutes per hour or 10l/s/p whichever is greater |  | local extract ventilation based on risk assessment when practical work involving fumes is planned | Local extract ventilation to provide 5ach during science experiments involving fumes. | Ventilation rate to suit occupancy | Ventilation rate to suit occupancy. Maximum air velocity for badminton to be achievable when badminton is played | openable windows required where possible | openable windows required where possible, HSE guidance applies | intermittent extract of 6l/s per WC/urinal and 15l/s per shower/bath | In toilets and hygiene rooms: intermittent extract of 6l/s per WC/urinal and 15l/s per shower/bath or 10ach whichever is greater | Ventilation can be variable but must be able to extract at 5ach when required
Acoustic requirements table |  | N/A |  | A1.40/60 | A1.45/65 | A2.40/60 | A3.35/60 | A3.40/60 | A4.30/55 | A4a.30/55 | A3.45/65 | A3.50/65 | A5.50/65 | A5.40/60 | A6.35/60 | A6.40/60 | A6.45/65 | A7.35/60 | A7.35/55 | A8.35/55 | A8.30/55
Type of room |  |  |  | Quiet study areas in libraries, Study rooms (individual study, withdrawal, remedial work, teacher preparation), Control room not used for recording (where visual and audio communica-tion with adjacent room is required) | Offices, staff rooms, medical rooms | Meeting rooms, Interviewing/ counselling rooms, video conference rooms | All classrooms, class bases, playrooms, general teaching areas, small group rooms, language laboratories, seminar rooms, tutorial rooms, Lecture rooms, Control room not used for recording (where visual and audio communica-tion with adjacent room is not required) | All light practical teaching spaces, including Science laboratories, Electronics/control, textiles, graphics, design/resource areas, ICT rooms, Art; food rooms; All open-plan areas; Resource areas | Teaching spaces specifically designed for use by students with special hearing or communication needs | Teaching spaces specifically designed for use by students with special hearing or communication needs off quiet corridors in special schools or isolated resourced provision | Atria, circulation spaces (including those used for circulation and socialising but not teaching and learning); Corridors, stairwells, Coats and locker areas | Toilets | Swimming pools, School kitchens, changing areas | Resistant materials, CADCAM areas | Primary music classroom | Activity Studio, Dance studio, Gymnasium, sports hall - not used for examinations | Dining rooms | Assembly halls, multi-purpose halls (drama, PE, audio/visual presentations, assembly, occasional music, examinations), Sports hall used for examinations, Drama Studios | Control room for recording | Music practice/group rooms, Performance/ recital room, Secondary school music classroom | Ensemble rooms, Recording studio
Room classification for the purpose of airborne sound insulation | Activity noise |  |  | Low | Low | Low | Average | Average | Average | Average | Average | Average | High | High | High | High | High | High | High | Very high | Very high
| Noise tolerance |  |  | Medium | Medium | Low | Medium | Medium | Low | Low | Medium | Medium | High | High | Medium | Medium | Medium | Low | Low | Low | Low
Minimum Dw (dB) (between spaces) | New build | Contractor to specify with reference to Acoustic Performance Standards for PSBP. Minimum for spoaces of same type shown |  | 40 | 40 | 45 | 45 | 45 | 50 | 50 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 55 | 55 | 55 | 55
| Refurbishment |  |  | 30 | 30 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 45 | 45 | 45 | 50 | 50 | 50 | 50
Maximum indoor ambient noise level for Mech Vent, and for Nat Vent when nat vent paths are shut, to achieve 1500ppm Carbon Dioxide concentration (see FOS) | New build | nat vent and hybrid systems may exceed these figures by 5dB when nat vent paths are open |  | 40 | 45 | 40 | 35 | 40 | 30 | 30 | 45 | 50 | 50 | 40 | 35 | 40 | 45 | 35 | 35 | 35 | 30
| Refurbishment |  |  | 45 | 45 | 45 | 40 | 45 | 35 | 35 | 45 | 50 | 50 | 45 | 40 | 45 | 45 | 40 | 40 | 40 | 35
Maximum impact sound pressure level L’w Sound entering from above | New build |  |  | 60 | 65 | 60 | 60 | 60 | 55 | 55 | 65 | 65 | 65 | 60 | 60 | 60 | 65 | 60 | 55 | 55 | 55
| Refurbishment |  |  | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Either: |  | Contractor to identify which measure is being used and mark other as N/A
Minimum composite Rw (dB) of corridor** wall, glazing and ventilators in walls with ventilators | New build |  |  | 33 | 33 | 33 | 33 | 33 | 38 | 33 | N/A | N/A | N/A | 33 | 38 | 33 | 33 | 38 | 38 | 38 | 38
| Refurbishment |  |  | 30 | 30 | 30 | 30 | 30 | 35 | 30 | N/A | N/A | N/A | 30 | 35 | 30 | 30 | 35 | 35 | 35 | 35
or:
Minimum composite Rw (dB) of corridor** wall and glazing without ventilators | New build |  |  | 40 | 40 | 40 | 40 | 40 | 45 | 40 | N/A | N/A | N/A | 40 | 45 | 40 | 40 | 45 | 45 | 45 | 45
| Refurbishment |  |  | 35 | 35 | 35 | 35 | 35 | 40 | 35 | (N/A) | (N/A) | (N/A) | 35 | 40 | 35 | 35 | 40 | 40 | 40 | 40
Minimum Dn,e,w – 10logN dB for ventilators in walls where applicable | New build and refurbishment |  |  | 32 | 32 | 32 | 32 | 32 | 37 | 32 | N/A | N/A | N/A | 32 | 37 | 32 | 32 | 37 | 37 | 37 | 37
Notes | ** excluding foyers | [8 empty] | See doorset note. Corridors are assumed to be relatively quiet
Minimum Dw (dB) new build (figures for refurbishment in brackets) |  |  |  | Activity noise in source room from Table 1.1
|  |  |  | Low | Average | High | Very high from music
Noise tolerance in receiving room |  | High |  | N/A | 35 (30) | 5. 45 (35) | 50 (45)
from Table 1.1 |  | Medium |  | 1. 40 (30) | 3. 45 (35) | 6. 50 (45) | 55 (45)
|  | Low |  | 2. 45 (35) | 4. 50 (40) | 7. 55 (50) | 8. 55 (50)
Acoustics (Reverberation Time) Table |  |  |  | R04 | R05 | R06.1 | R06.2 | R08 | R08.1 | R08.2 | R10 | R10.1 | R10.2 | R10.3 | R12 | R12.1 | R15 | R20 | R00
Type of room |  |  |  | Teaching spaces specifically designed for use by students with special hearing or communication needs (note 4) and basic teaching spaces in special schools other than practical spaces | Control room for recording; Open plan teaching areas | Nursery and primary school classrooms, class bases, playrooms, small group rooms; special school practical rooms; music practice/ group rooms ≤ 30m3 | Ensemble rooms, Live rooms | Meeting rooms, Interviewing/ counselling rooms, video conference rooms. | Study rooms; All secondary teaching areas except music classrooms, drama studios, ensemble rooms and live rooms, including music practice/group rooms > 30m3; teacher preparation | Assembly halls, multi-purpose halls (drama, PE, audio/visual presentations, assembly, occasional music) | Secondary music classrooms; Primary music room, Drama studios. Administration and ancillary spaces including Offices, staff rooms, medical rooms | Libraries | Dining space | Performance/ recital room | Open Plan Resource / Breakout areas | Dance studios, activity studios, movement studios | Toilets; atria; coats and locker areas (including those used for circulation and socialising but not teaching and learning); kitchens; activity studio, gymnasium | sports hall, Swimming pools | circulation spaces corridors and stairwells)
Reverberation Time Tmf (seconds) | new build |  |  | N/A | ≤0.5 | ≤0.6 | 0.6 - 1.2 | ≤0.8 | ≤0.8 | 0.8 - 1.2 | ≤1.0 | 1 | ≤ 1.0 | 1.0 - 1.5 | ≤1.2 | ≤1.2 | ≤1.5 | ≤2.0 | N/A
| refurbishment |  |  | (≤ 0.4) | (≤0.5) | (≤0.8) | (0.6 - 1.2) | (≤0.8) | (≤1.0) | (0.8 - 1.2) | (≤1.0) | (≤1.2) | (≤1.5) | (1.0 - 1.5) | (≤1.2) | (≤1.5) | (≤2.0) | (≤2.0) | N/A
≤ 0.4 averaged from 125 Hz to 2 kHz and <0.6 in every octave band |  |  |  | yes | no | no | no | no | no | no | no | no | no | no | no | no | no | no | no
Absorption calculated in accordance with Approved Document E |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | yes
Notes |  |  |  |  | To be in accordance with Section 2.8 of Acoustic Standards for PSBP | [9 empty] | To be in accordance with Section 2.8 of Acoustic Standards for PSBP
NOTES |  | Note 1 | For refurbishment; account should be taken of the Asset Management Plan and feed back from the Authority and Occupants to determine requirements. Guidance should be taken from the requirement for a new building. The Contractor should enter the proposed change/standard in the relevant box in the "Contractor Proposal" column of the Compliance Check area.
|  | Note 2 | The Contractor must determine if acoustic finishes are required, depending on space use and adjacencies
|  | Note 3 | For corridors and stairwells Reverberation Time cannot be measured and requirements are given in terms of area of absorption . See Section 2.7 of Facilities Output Specification
|  | Note 4 | As defined in Acoustic Standards for PSBP, replacing BB93