JSP 319
Joint Service Publication for the Safe Storage and Handling of Gases
Part 2: Guidance
Part 2 - Guidance - Gases General & Liquefied Petroleum Gas (LPG)

JSP 319 Part 1(v4.4 Nov 19) JSP 319 Part 1(v4.4 Nov 19) JSP 319 Part 1(v4.4 Nov 19) JSP 319 Part 1(v4.4 Nov 19)

JSP 319 Part 2 (v5 Dec 22)

# Foreword JSP 319 Part 2, v5

JSP 319, Part 2 provides guidance in accordance with the policy set out in Part 1 of this JSP; the guidance is sponsored by the Defence Safety Authority for the End to End[1] process of gas storage facilities for transportable gas cylinders, bulk cryogenic storage pressure vessels and bulk LPG storage pressure vessels in the Land domain. It provides policy compliant business practices which should be considered best practice in the absence of any contradicting instruction. However, nothing in this document should discourage the application of sheer common sense.
[1] End to End Includes: Transportable gas cylinders when in a station / central establishment store. Bulk cryogenic gases and associated pipelines (up to 1st stage regulator) Independent bulk LPG and associated pipelines (up to 1st stage regulator). End to End does not include: Transportable gas cylinders in-use / when connected to a manifold / system. (Operating Authority / Equipment, Platform Sponsor / MMO / Trade Sponsor Responsibility as applicable) Natural gas storage and pipeline transportation (DIO responsibility) Distribution of gases within an equipment, platform or building (Operator / DIO) Transportation of gas cylinders - Transport of Dangerous Goods (iaw DGM)

# Acknowledgements

Diagrams reproduced from Liquid Gas UK publications, with kind permission of the Liquid Gas UK. For more information visit: https://www.liquidgasuk.org/. Diagrams reproduced from the British Compressed Gas Association (BCGA) publications, with kind permission of the BCGA. For more information visit: www.bcga.co.uk.

# Amendment Sheet

Amendment		Incorporated By
No	Date	Name	Signature	Date
1	Dec 07	WO1 (SSM) Gaunt		Dec 07
2	Jan 09	WO1 (SSM) Gaunt		Jan 09
3	Jan 10	WO1 (SSM) Garner		Jan 10
4	Jan 11	WO1 (SSM) Garner		Jan 11
5	Mar 12	WO1 (SSM) Eversfield		Mar 12
6	Mar 13	WO1 (SSM) Eversfield		Mar 13
7	Apr 15	WO1 (SSM) Costello		Apr 15
8	Jun 16	WO1 (SSM) P Franks		Jun 16
9	Nov 17	WO1 (SSM) P Franks		Nov 17
10	Nov 18	WO1 (SSM) I Baynham		Nov 18
11	Nov 19	WO1 (SSM) I Baynham		Nov 19
12	Jan 21	WO1 (SSM) M Bryson		Jan 21
13	Dec 21	WO1 (SSM) M Bryson		Dec 21
14	Dec 22	WO1 (SSM) M Bryson		Dec 22

# Contents:

Pat 1: Directive
Foreword
Chapter 1	Legislation
Chapter 2	MOD Gases Organisation
Chapter 3	Accident / Incident / Dangerous Occurrence Reporting
Chapter 4	Training
Chapter 5	Emergency Situations, Preparation and Actions
Chapter 6	Siting, Commissioning, Transfer, and Decommissioning

Part 2: Guidance

Foreword
	Acknowledgement
	Amendment Sheet
	Contents

Preface
	How to use this JSP
	Coherence with other Defence Authority Policy and Guidance
	Further Advice and Feedback - Contacts
	Glossary
	Introduction to JSP 319
	Applicability
	Format
	Editorial
	Annex A: Definitions
	Annex B: Abbreviations

Chapter 1 Introduction to Gases
	Scope
	General
	Hazards
	Hazardous Gas Monitoring
	Gas Classification
	Hazards to the Environment
	Health and Safety
	British Compressed Gases Association (BCGA)
	Bibliography
	Annex A: Properties of Industrial Gases
	Annex B: Waste Gas Discharge to Atmosphere

Chapter 2 Personal Protective Equipment (PPE)
	Scope
	General
	Specified PPE
	Bibliography
	Annex A: Recommended PPE / Clothing for use in a Cryogenic Environment

Chapter 3 Identification of Gas Receptacles
	Scope
	General
	Standard Identification Marking
	Additional Identification Marking
	Bibliography
	Annex A: Cylinder Test Rings
	Annex B: Stamp Markings for Compressed Gases
	Annex C: Stamp Markings for Acetylene Cylinders
	Annex D: Stamp Markings for LPG Cylinders
	Annex E: Examples of Diamond Hazard Labels used for Gases
	Annex F: Examples of Labels used When Transporting Liquefied Gases
	Annex G: Examples of Additional Labels Used on Gas Receptacles

Chapter 4 Procurement, Maintenance & Disposal of Gas Cylinders
	Scope
	Manufacture and Procurement of Transportable Gas Cylinders
	Valve Protection Devices
	Repair and Testing of Gas Cylinders
	Disposal of Gas Cylinders
	Bibliography

Chapter 5 Gas Production and Cylinder Filling
	Scope
	General
	Gas Production Equipment
	General Requirements for Filling Cylinders
	Filling Procedures
	Bibliography
	Annex A: Contractors Authorisation to Fill Cylinders

Chapter 6 Gas Testing
	Scope
	General -Testing
	Aviation Gases and Cryogenic Liquids - Testing
	Compressed Natural Breathing Air (CNBA); Diving Gases and Gas Mixtures - Testing
	Other Cryogenic Liquids - Testing
	Calibration Gas Mixtures - Testing
	Medical Gases - Testing
	Industrial Gases
	Liquefied Petroleum Gases
	Refrigerants
	Welding and Cutting Gases
	Test and Sampling Equipment
	Bibliography
	Annex A: Odour Assessment of Liquid Oxygen (LOx) and Liquid Nitrogen (LiN)
	Annex B: Visual Examination of Liquid Oxygen (LOx) and Liquid Nitrogen (LiN)
	Annex C: Odour Assessment of Gaseous Oxygen, Compressed Natural Breathing Air, or Diving Gases
	Annex D: DE&S Oils Lubricants & Gases Nominated Test Laboratory
	Annex E: Compressed Natural Breathing Air (CNBA), for Diving Gases and Gas Mixtures
	Annex F: Marine Life Support, Marine Firefighting, Emergency Escape on Board Ships and Submarines
	Annex G: Aviation Emergency Breathing Apparatus (BA)
	Annex H: DFRMO Firefighting CNBA
	Annex I : Workplace use CNBA

Chapter 7 Handling and Use
	General
	Gas and Cylinder ‘Lifing’
	Precautions and User Procedures
	Handling
	Leak Detection
	Discharging Gas
	Bibliography
	Annex A: Gas Storage Equipment

Chapter 8 Transportation
	Scope
	General
	Inspection and Testing of Gas Cylinders
	Transportation by Road
	Transportation by Sea
	Transportation by Air
	Reporting Accidents / Incidents
	Bibliography
	Annex A: Transportation by Road - ADR Loads Exemption Limits
	Annex B: Net Quantity for Transport

Chapter 9 Gas Cylinder Storage
	Scope
	Health, Safety, Environmental and Security Arrangements
	Outdoor Gas Cylinder Storage Compounds - Siting
	Outdoor Gas Cylinder Storage Compounds - Construction and Layout
	Outdoor Gas Cylinder Storage Compounds -Signage
	Outdoor Gas Cylinder Storage Compounds - Fire Safety
	Outdoor Small Quantity Gas Cylinder Stores (e.g. Cages)
	Gas Cylinder Storage Inside Specially Constructed Buildings - Siting
	Gas Cylinder Storage Inside Specially Constructed Buildings - Construction and Layout
	Gas Cylinder Storage Inside Specially Constructed Buildings - Signage
	Gas Cylinder Storage Inside Specially Constructed Buildings - Fire Safety
	Indoor Small Quantity Gas Cylinder Stores (e.g. Cabinets)
	Bibliography
	Annex A: Industrial Gas Cylinder Storage Facility Signage
	Annex B: Minimum Recommended Safety Separation Distance for Industrial Gas Cylinders
	Annex C: Design and Layout for Industrial Gas Cylinder Storage Areas - Examples

Chapter 10 Organisation and Management of Gas Cylinder Storage Compounds
	Scope
	Gas Cylinder Grouping / Segregation / Identification.
	Cylinder Orientation and Security
	Gases
	Considerations of High or Low Temperature Storage
	Other Storage Considerations
	Management of Gas Cylinders Storage Compounds
	Inspection of Gas Cylinders and Gas Cylinder Stores
	Bibliography

Chapter 11 Organisation and Management of Bulk Cryogenic Liquid Storage Compounds
	Scope
	Cryogenic Liquids, Health, Safety, Environmental and Security Arrangements
	Cryogenic Compounds-Siting
	Cryogenic Compounds, Construction and Layout
	Cryogenic Compounds - Signage
	Cryogenic Compounds - Fire Safety
	Cryogenic Compounds - Bulk Cryogenic Storage Vessels
	Bibliography
	Annex A: Inert Gas Asphyxiation

Chapter 12 Cryogenic Liquids
	Scope
	Properties and Hazards of Cryogenic Liquids, General
	General Class Hazards of Cryogenic Liquids
	Properties and Hazards of Liquid Oxygen
	Properties and Hazards of Liquid Nitrogen
	Properties and Hazards of Liquid Argon
	Properties and Hazards of Carbon Dioxide
	Safety Management of Cryogenic Compounds
	Bibliography

Chapter 13 Aviation Gases
	Scope
	General
	Aviation Ground Supply Gas Cylinders
	Aviation Gas Cylinders with an Airborne Application
	Bibliography

Chapter 14 Refrigerant and Fluorinated Gases (F-Gases)
	Scope
	EU, UK and MOD Policy
	Refrigerants and Refrigerant Cylinders
	Bulk Storage of Refrigerants
	Recovery Cylinders
	Bibliography

Chapter 15 Medical Gases
	General
	Medical Gases, and Gas Cylinder Properties
	Contaminated Medical Gas Cylinders
	Storage of Medical Gas Cylinders
	Bibliography

Chapter 16 Diving Gases
	Scope
	General
	Quality Assurance
	Handling and Use
	Bibliography

Chapter 17 Introduction to LPG
	Scope
	Defence Infrastructure Organisation (DIO)
	Liquefied Petroleum Gas Trade Association
	Safe Handling of LPG
	LPG Medical First Aid
	Safety Signs and Warning Notices

Chapter 18 Liquefied Petroleum Gas (Cylinders)
	Scope
	LPG Cylinder Marking and Labelling
	LPG Cylinder Maintenance
	LPG Cylinder Handling
	LPG Cylinder Maintenance
	LPG Gas cylinder Storage - General Requirements
	Outdoor LPG Cylinder Compounds, LPG Cylinders (< 20kg Individual Size; Total Storage Capacity >400kg)
	Outdoor LPG Cylinder Compounds, LPG Cylinders Storage Capacity (> 50kg < 1000kg)
	Outdoor LPG Cylinder Compounds - Storage of LPG Cylinders Within a MTFI
	LPG Cylinder Storage, Inside Specially Constructed Buildings
	LPG Cylinder Storage, Inside Existing Buildings
	Gas & LPG Cylinder Storage on Operations and Exercise
	Additional Requirements for Gas Cylinder Storage on HM Ships and Other Vessels
	Bibliography
	Annex A - Minimum Recommended Safety Separation Distances for LPG Gas Cylinders
	Annex B - Design and Layout for LPG Gas Cylinder Storage Areas - Examples
	Annex C - Unit Guide to the Safe Handling and Storage of LPG Cylinders on Exercise

Chapter 19 - Bulk LPG
	Scope
	Notification to Civilian Authorities of LPG Facilities
	Bulk LPG Road Delivery Precautions
	Bulk LPG Siting Boards and Siting Requirements
	Bulk LPG Installation Design
	Demarcation of Site Responsibilities
	Automotive Mechanical Transport Fuelling Installation - General
	Operations
	Training
	Annex A: Minimum Separation Distances for Bulk LPG Vessels
	Annex B: Bulk LPG Vessel Compound Design Examples
	Annex C: Small Bulk LPG Vessel Adjacent to a Building

Chapter 20	Bibliography (LPG) Chapter 17,18,19

# Preface

Chapter Sponsor - DSFA WO Policy

## How to use this JSP

JSP 319 lays down the standards of practice to be observed within the MOD for the storage and handling of all Industrial Gases including Liquefied Petroleum Gas. It is designed to be used by staff responsible for the storage and handling of Industrial Gases stored in cylinders, LPG stored in bulk storage vessels and Cryogenic liquids stored bulk cryogenic storage tanks.

The JSP is structured in two parts:

  1. Part 1 - Directive, which provides the direction that must be followed in accordance with Statute, or Policy mandated by Defence or on Defence by Central Government.

  1. Part 2 - Guidance, which provides the guidance and best practice that will assist the user to comply with the Directive(s) detailed in Part 1.

Related JSPs	Title
JSP 319 Pt 1	Joint Service Publication for the Safe Storage and Handling of Gases, Part 1: Directive.
DSA 01.1	Defence Policy for Health, Safety and Environmental Protection
DSA 02 ,DSA 03	Fuels & Gas Safety & Environmental Regulations & DCOP's
JSP 418	Management of Environmental Protection in Defence
JSP 375	Management of Health and Safety in Defence

## Coherence with other Defence Authority Policy and Guidance

Where applicable, this document contains links to other relevant JSPs, some of which may be published by different Defence Authorities. Where particular dependencies exist, these other Defence Authorities have been consulted in the formulation of the policy and guidance detailed in this publication.

## Further Advice and Feedback- Contacts

The owner of this JSP is Defence Support, Defence Strategic Fuels Authority (DSFA). For further information on any aspect of this guide, or questions not answered within the subsequent sections, or to provide feedback on the content, contact in the Subject Matter Expert / Chapter Sponsors promulgated at the front of each Chapter, or:

Job Title	Email	Phone
DSFA – Technical Gases Mgr	Joseph.Lam102@mod.gov.uk	030 0160 8913
DSFA – JSP Editor	Mark.bryson655@mod.gov.uk	030 0153 5993

## Glossary

Scope. This section provides the standard definitions and abbreviations for specialist terminology used relating to the storage, handling and use of the range of gases used within the MOD.

Source. Definitions used in this publication are mainly derived directly from legislation, Codes of Practice and Guidance Notes. In addition, NATO terminology has been introduced where appropriate. The relevant source is quoted wherever possible.

Primacy. In deriving the definitions used in this publication, several meanings have been found to exist for the same expression. Accordingly, the following table of accession has been adopted:

  1. UK legislation.

  1. International Standards Organisation (ISO).

  1. Economic Commission for Europe (ADR).

  1. European Standards (CEN).

  1. British Standards Institute (BSI).

  1. Trade Associations, including BCGA, Liquid Gas UK and EIGA

  1. NATO Terminology (APP-1).

  1. MOD (e.g. APs, JAPs, JSPs, SRPs, etc).

Availability. JSP 319 is available electronically from the Defence Net (defnet). A controlled version is available on the World Wide Web (Internet).

Units that require JSP 319 in CD-ROM format are expected to ‘burn’ off copies as required at a local level. Units that either have no access to the Intranet or the facility to ‘burn’ CD-ROM’s should staff their requirement through the chain of command. Exceptionally CD-ROM copies of JSP 319 can be obtained from the JSP 319 Technical Editor -Mark.bryson655@mod.gov.uk.

Abbreviations and terms defined in this publication are contained in Annexes A and B. In this publication, the following terms have the definitions assigned to them irrespective of any other meanings that may be given elsewhere. The source publication has been identified where applicable. To minimise confusion, wherever practical the terminology used by civilian industry or incorporated into legislation and standards are used.
## Introduction to JSP 319

Scope. This manual lays down the standards of practice to be observed within the MOD for the storage and handling of Industrial Gases including Liquefied Petroleum Gas and cryogenic liquids.

Sources. The regulations contained within JSP 319 are derived from international and national legislation; international, NATO and national standards; industry Codes of Practice and Guidance Notes.

Authority. JSP 319 is produced and maintained by the Defence Strategic Fuels Authority under the parameters of the DSA FGSR Stakeholder Committee as defined in DSA 01.1 and DSA 02 & DSA 03.

Maintenance. JSP 319 will be maintained on the Defence Net (defnet) and will be revised on an as-required basis. All hard copies of JSP 319 are uncontrolled. To check the latest amendment status reference should be made to the defnet or to Mark.bryson655@mod.gov.uk

Equality and Diversity Impact Assessing Statement. This policy has been Equality and Diversity impact assessed in accordance with the department’s equality and diversity impact assessment tool against: "Part 1 Assessment only - no diversity impact found."

## Applicability

The Secretary of State for Defence issues a policy statement on Safety, Health, Environmental Protection and Sustainable Development in the MOD which sets out the strategic principles, duties and governance to be applied throughout the MOD. This policy statement is published in DSA 01.1 SHEP. The MOD policy for fuel and gases is promulgated by the Defence Fuels and Gases Stakeholder Committee (DF&G SC) in the form of a domain specific publication - DSA 02 & DSA 03. The specific MOD policy and regulations relating to the End to End[2] storage, and handling of gases are detailed in JSP 319, Part 1. JSP 319 regulations shall be applied to the storage & handling of gas and LPG products by the three Services, Defence Equipment and Support (DE&S), Central TLB, and Defence Agencies. The regulations shall also apply to contractors, and their personnel, operating on the MOD estate and to non-public activities/encroachments (such as flying clubs).
[2] End to End Includes: 1. Transportable gas cylinders when in a MOD station / MOD central establishment store. 2. Bulk cryogenic gases and associated pipelines (up to 1st stage regulator) 3. Bulk LPG and associated pipelines (up to 1st stage regulator). End to End does not include: 1. Transportable gas cylinders that are in-use. (Operating Authority / Equipment, Platform Sponsor / MMO / Trade Sponsor Responsibility as applicable) 2. Natural gas storage and pipeline transportation (DIO responsibility) 3. Distribution of gases within an equipment, platform or building (Operator / DIO) 4. Cylinders that are in-carriage (Transport carriage of Dangerous Goods iaw DGM)

Transportation. All gases and pressure receptacles, including gas cylinders, aerosols, tanks and MEGC's are classified as dangerous goods. JSP 800 – Defence Movement and Transport Regulations JSP 800 are always to be consulted when transporting dangerous goods detailed within this publication Part 2 Chapter 8.

Exceptions. These regulations do not cover the internal use of Gas Products aboard ships or vessels, or in aircraft operated by the Services or specialist contractors or agencies, or the repair of MOD vehicles or aircraft for which special regulations apply. Such special regulations shall be based on this publication. Similarly, where the Services need to operate at locations which require specific standards higher than those contained in this manual, then the higher standard shall be applied. Where applicable these specialist regulations/publications are referenced within JSP 319.

Outside UK. In countries, outside of the UK, the standards specified in this manual shall be applied unless the host nation requires a higher standard in which case that standard must be applied. In Germany, where the Status of Forces Agreement (SOFA) has precedence, all facilities must be constructed to German Standards with disregard to the regulations specified in this manual.

Specific Procedures. The main sections of the JSP 319 will detail the generic procedures to be used within the services and associated users. However, where storage handling procedures are not common across the services at this stage, they will be detailed in annexes or references covering the Land, Marine and Aviation environments. Where single-Service issues require the production of clarifying or complementary statements, policies or orders, these shall be based on the detail of this publication but should not repeat its contents. The JSP 319 shall have primacy over any such clarifying or complementary statements, policies or orders.

User Responsibilities. The responsibility for the safe use of gases lies with the “user” and their respective Trade Group Sponsor or equipment / platform Project Team (PT) as appropriate. “User” process should include safe operating procedures, (how gases interface with user equipment / processes), training, and auditing programmes (including Ready Use).

Note: Examples of users: - welding bays, medical centres, diving stores, LOx charging bays.

Operational Conditions. Some relaxation of the procedures detailed in the JSP 319 may be necessary under operational circumstances. However, as many of the regulations and procedures contained within the JSP are derived directly from legislation, exemption from the regulations would require the approval of the Secretary of State for Defence.

Parts. The JSP 319 consists of two main parts.

## Format

The format of this JSP is in accordance with JSP 101 and constructed to Defence Reform Unit (DRU) standardisation.

## Editorial

jsp 319 is published under the management control of Defence Support, DSFA as the MOD Regulations for storage, handling and use of gases. The chairman of the JSP 319 Working Group is responsible for the editorial content of this publication.

Editorial Working Group. An editorial Working Group is responsible for reviewing the content of JSP 319: Refer to Table 1.

Table 1 - Composition of JSP 319 Editorial Working Group.
Department	Members
UK STRATCOM - DSFA	DSFA COS - SO1 Chair JSP 319 WG
	DSFA Policy WO1 - Secretariat of JSP 319 WG
	DSFA Technical Gases Manager
DSA Fuels & Gas Safety Regulator	FGSR - Gas Auditor
DSA	NAVY SAFETY DDST CNTR- SDSIENG
	DSA-DLSR-MTSR-Reg-DG-SO2
Navy Comd HQ	SO2 Navy Log Infra
Army Comd HQ	SO2 Fuels, D Support, Army HQ
	64 Wks Gp RE, 516 STRE OC
	DFR-HQ SCP GM SR
Air Comd HQ (38 Gp)	SO2 38 Gp Fuels RO
UK STRATCOM	CESO EPSD A
Defence Equipment & Support (DE&S) / Defence Fuel & Food Services (DES LCS OILS, LUBRICANTS, AND GASES TEAM)	SCM SC Mgr
	SCM Inv Mgr 2
	Technical Team Manager
Defence Equipment & Support (DE&S)	AS-AC GSE1d
	TECH - AG DStan-SPM5
	DES Ships MCS - UEW
	Tech Spt DES Intertek
	DES TECH-QSEP HAZMAT-Sup
	DES LD CMO-Ops-Comply-RP
Defence Infrastructure Organisation (DIO)	DIO ODC - Eng Mech AH Sp
	DIO TS-Eng Mech 1a
Defence Support Group Stafford (DSG)	Cryogenics & Gas Manager / Defence Electronics & Components Agency
Additional Chapter Sponsors (SMEs)	As Required

Amendments. Amendments will be issued whenever required to reflect changes in legislation or other source documents. Proposed amendments to JSP 319 should be submitted through existing staff channels to the Editor of JSP 319.

## Reporting Amendments in JSP 319

Purpose. The purpose of this information is to provide users at all levels with a means of reporting unsatisfactory features in the JSP 319 and proposing an amendment. Reports are to be submitted using The MOD Form 765

Originator of report. Originators of reports are to raise one copy of the report. Once satisfied that the report contains all relevant detail, it is to be forwarded to the JSP 319 Editor mark.bryson655@mod.gov.uk. There is no requirement to provide a covering letter or additional correspondence with the report; unless the originator believes amplification of the report is necessary to assist the JSP 319 WG.

Action by JSP 319 WG. On receipt of the report, the JSP 319 WG is to investigate the content of the report and, if necessary, initiate amendment action through the Chapter
Sponsors and the Editor of JSP 319. On completion the Editor is to advice the originator the decision of the JSP 319 WG and the revision made if applicable.

# Annex A – Definitions

Term	Definition	Source
Access Apron	An area between the tank and a tanker where the process operating controls on both tank and tanker are accessible to the operator during filling/discharging. This area will normally have provision for containing or diverting a liquid spillage.	BCGA CP 36
Accident (Incident)	Any event which causes, or has the potential to cause injury, loss or damage to people, plant or premises.	JSP 375
ADR	European Agreement Concerning the International Carriage of Dangerous Goods by Road	ADR
Aerosol or Aerosol dispenser	Any non-refillable receptacle made of metal, glass or plastics and containing a gas, compressed, liquefied or dissolved, with or without a liquid, paste or powder, and fitted with a relief device allowing the contents to be ejected as solid or liquid particles in suspension in a gas, as a foam, paste or powder or in a liquid state or a gaseous state.	ADR
Air Separation Unit (ASU)	Air separation units produce nitrogen, oxygen and argon using air and electrical power as raw materials. While there are variations in the process details, reflecting desired product mix and other factors, all air separation units belong to one of two general process categories: / Cryogenic plants – Produce gas and liquid products using very low temperature distillation to separate air components and achieve the desired product purities. / Non-cryogenic plants – Produce gaseous products with near-ambient temperature separation processes that utilize differences in properties such as molecular structure, size or mass to generate oxygen or nitrogen.
Air compressor	A machine that draws in air at atmospheric pressure compresses it and delivers it at a higher pressure.
Anesthetic gas	Gas with narcotic characteristics, for medical use. / EXAMPLE: Cyclopropane.	ISO 10286
Analgesic gas	Gas with pain-relieving characteristics, for medical use. / EXAMPLE: Nitrous oxide.	ISO 10286
Asphyxiant gas	Gas which can cause suffocation when inhaled by man or animals. / Note: Although most gases, with the exception of air, oxygen and a few others, are asphyxiant, the term is mainly used for gases not connected with other hazards, flammability, toxicity, etc.	ISO 10286
Authorised Person – Petroleum	A person employed by, or commissioned by the Works Services Manager or MOD, and appointed for the purpose of implementing the MOD Safety Rules and Procedures by the Commanding Officer/Head of Establishment/Officer in Charge.	JSP 375 Vol 3
Authorising Engineer –Petroleum	A suitably experienced chartered mechanical engineer experienced in petroleum handling systems, employed or commissioned by the Works Services Manager or MOD, and appointed by the Commanding Officer, Head of Establishment or Officer in Charge to ensure safety of petroleum work for the base	JSP 375 Vol 3
Batch	A quantity of cylinders that are filled from the same charge from the same source.
Breathing Apparatus	Apparatus designed to enable the wearer to work and breathe without harmful effects in a non-life supporting atmosphere by supplying breathable quality air via an airline or pressurised cylinder.	BR 1754
Breathing gas	Gas used in breathing apparatus to aid breathing. / EXAMPLES: Air, nitrogen/oxygen mixtures
BLEVE	Boiling Liquid Expanding Vapour Explosion – the explosive release / of expanding vapour and boiling liquid following the catastrophic / failure of a pressure vessel (cylinder) holding a pressurised liquefied / gas such as LPG. On contact with a source of ignition this then / causes an unconfined vapour cloud explosion.	BCGA GN15
Bundle (of cylinders)	An assembly of cylinders that are fastened together and which are interconnected by a manifold and carried as a unit. The total water capacity shall not exceed 3000 litres except that bundles intended for the carriage of toxic gases of Class 2 shall be limited to 1000 litres.	ADR
Burst pressure	Highest pressure reached in a cylinder during a burst test	ISO 10286
Cartridge	LPG: / A non-refillable container of less than 1.4 litre water capacity. Often fitted with a pierceable diaphragm or a self-sealing valve. / Gas: / See Gas Cartridge.
CE Mark(ing)	A EC Declaration of Conformity, by means of adding a CE Mark to a PPE product	EC Legislation
Combustible Gas Indicator (Explosimeter)	An instrument used to measure the concentration of flammable gas.
Compressed air	Compressed air produced by an air compressor. Normally produced to a low specification (suitable for tool use) and is not suitable for breathing purposes.	Def Stan 68-284
Competent Person	A person with sufficient technical knowledge or experience to prevent danger or, where appropriate, injury, during his or her work.	JSP 375
	A competent individual person (other than an employee) or a competent body of persons incorporated or unincorporated. Responsible for preparing or certifying the suitability of a written scheme of examination and for carrying out an examination in accordance with the written scheme of examination.	PSSR
Compressed gas	Gas, which, when packaged under pressure for transport, is entirely gaseous at all temperatures above –50ºC.Note: This category includes all gases with a critical temperature less than -50ºC	ISO 10286 / (BS) EN 1920
Container	A cylinder or cartridge.
	A storage tank, replenishment trolley or flask used for the storage and transportation of liquid oxygen or liquid nitrogen.
	A portable container, including small cans and bottles, drums, portable tanks and tank containers of any size not connected to a process.	HS(G)51
Corrosive Gas	A corrosive gas is one which, on direct contact, may harm human tissue. Many corrosive gases may also react with certain materials of construction causing material damage and possible failure. Corrosive gases only react with a material in the presence of water or moisture from the atmosphere or other sources.
	UN Definition – Gases which: / (a). Are known to be so toxic or corrosive to humans as to pose a hazard to health; or / (b). Are presumed to be toxic or corrosive to humans because they have a LC 50 value for acute toxicity equal to or less than 5 000 mL/m³ (ppm). / Gases or gas mixtures meeting the criteria for toxicity completely owing to their corrosivity are to be classified as toxic with a subsidiary corrosivity risk. Class 2, Division 2.3.	ADR
Critical pressure	The minimum pressure required to liquefy a gas at its critical temperature.
Critical temperature	The temperature above which the substance cannot exist in the liquid state. / Note: For gas mixtures the corresponding term is pseudo-critical temperature.	ISO 10286 / ADR
Cryogenic liquid	Gas which liquefies at 1.013 bar at a temperature below –30°C. / Note: Cryogenic fluids can be stored or transported only in thermally insulated containers. These gases are also known as liquefied gases or liquefied refrigerant gases, as appropriate.
Cylinder	A transportable pressure receptacle of a water capacity not exceeding 150 litres.	ADR
Dangerous Area	An area in which there exists, or may exist, a dangerous atmosphere which in turn is defined as an atmosphere containing: / a. Any flammable gases or vapour in a concentration capable of ignition. / b. A concentration of toxic gas above prescribed limits. / c. An atmosphere containing insufficient oxygen for normal respiration.
Dangerous Occurrence	A specific, unplanned, uncontrolled event which has the potential to cause injury or damage and is listed in Schedule 2 of the Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 1995.	JSP 375
Decant	The filling or trans-filling from one gas cylinder to another
Decant cylinder	Cylinder, normally for refrigeration gases, cleaned to a high standard, suitable for the temporary storage of a gas from a system.
Decomposition	Chemical reaction whereby a substance breaks down into its constituent elements. In the case of acetylene this means carbon and hydrogen. This reaction gives out a great deal of heat.
Design pressure	Pressure used in the formula for the calculation of the minimum wall thickness of a cylinder. / Note: In most cylinder design regulations it is the test pressure	ISO 10286
Developed pressure at Tmax	Pressure developed by the gas contents in a cylinder at a uniform temperature of Tmax / Note: Tmax is the expected maximum uniform temperature in normal service as specified in international or national cylinder filling regulations.	ISO 10286
Dewar flask	A thermally insulated container. It consists of two flasks, one placed inside the other, with a vacuum between. The vacuum prevents the conduction of heat from one flask to the other. For greater efficiency the flasks are silvered to reflect heat. The substance to be kept hot or cold, e.g. a cryogenic liquid, is contained in the inner flask.
Dew point	The temperature at which dew, or condensation, forms on cooling a gas. It is a measurement taken at normal atmospheric pressure (1.013 bar). / Note: For temperatures below 0ºC the term ‘Frost point’ should strictly be used, but the term Dew point is often used to include Frost points.	Def Stan 68-284
Dissolved Acetylene	Acetylene dissolved in acetone or dimethylformamide.	(BS) EN ISO 3807
Dissolved gas	Gas which when packaged under pressure for transport is dissolved in a liquid phase solvent	ISO 10286
Downstream User	Someone who uses substances in the course of his industrial or professional activities. / Note 1: A Downstream User is, by definition, not a Manufacturer, or an Importer (into the EU) of chemicals. / Note 2: Some of the duties of a Downstream User may apply to Distributors, Retailers and Storage.	REACH Regulations
Dunnage	Loose wood, matting or similar material used to keep cargo in position, typically in a ships hold.
Earthing Boss	A brass bolt or lug brazed to a vessel to which the earthing system is attached.
Entonox™	A trade name used by BOC Gases to identify a medical gas mixture of 50% Nitrous Oxide and 50% Oxygen.
Expendable Container	An LPG container that cannot be refilled (see also Cartridge).
Explosives area	An area used for the storage, handling and processing of explosives that are usually enclosed by a security fence.	JSP 482
F Gas	A Fluorinated Greenhouse gas controlled under the Kyoto Protocol.
Filler	Person or persons responsible for inspection prior to, during and immediately after filling and who has received an appropriate level of training for the work involved and has access to all necessary data for the cylinder, valve and all other fittings used.	(BS) EN 1919 / (BS) EN 1920
Filling pressure	Pressure to which a cylinder is filled at the time of filling. / Note: It varies according to the gas temperature in the cylinder, which is dependent on the charging parameters and the ambient conditions.	ISO 10286 / (BS) EN 1920
Filling ratio	Ratio of the mass of gas to the mass of water at 15°C that is filled in a gas cylinder ready for use. / Note: Synonyms are filling factor and filling degree, often expressed in kg/l or similar.	ISO 10286 / ADR / (BS) EN 1919
Fire wall	A wall, screen or partition erected in the open air to help protect containers of flammable liquid (LPG) from heat radiating from a nearby fire, and/or to ensure adequate dispersion distance from buildings, boundaries, sources of ignition etc for flammable liquid or vapour leaking from any container. A fire wall in this context does not include a wall intended only to protect buildings and other features in the vicinity from a fire at a container storage area.	HS(G) 51
Flameproof	Apparatus that will withstand an internal explosion of the flammable gas or vapour which may enter it, without suffering damage and will prevent the transmission of flame to the external flammable gas or vapour for which it is designed, through any joints or structural openings in the enclosure.
Flame Arrestor	A device which arrests a flame front (caused by flashback or decomposition) and which is suitable for the most severe type of flame which may occur.
Flammable gas	Gases which burn readily in the presence of oxygen or air and in certain admixtures are explosive.
Flashback	Occurs when flame from a torch burns back into the tip, the torch or the hose. It is often accompanied by a hissing or squealing sound with a smoky or sharp-pointed flame.
Frost point	See ‘Dew point’.	Def Stan 68-284
F & L	Fuels & Lubricants
Full gas cylinder	A gas cylinder charged to its working pressure or, in the case of a liquefiable gas, a cylinder filled to its tare weight.
Gas	Any substance that is completely gaseous at 1.013 bar and 20ºC or has a vapour pressure exceeding 3 bar at 50ºC. / Note: The word substance encompasses pure substances as well as mixtures.	ISO 10286
Gas cartridge	Any non-refillable receptacle containing, under pressure, a gas or a mixture of gases. It may be fitted with a valve.	ISO 10286 / ADR
Gas free	A vessel or similar confined space is considered to be gas free if the concentration of combustible vapours present is below one per cent of the lower explosive limit as measured by an accurate and recently calibrated indicator, combustible gas. / Note: Gas free does not mean non-toxic
Hazardous Area	An area in which explosive gas – air mixtures are, or may be expected to be, present in quantities as to require special precautions to instigated to prevent their ignition. Such areas are to be Designated and appropriately signed.	JSP 375 Vol 3
Hazard Division (HD)	A division of the United Nations Dangerous Goods Class definition indicating the main type of hazard to be expected in the event of an accident.
Heliox	A gas comprising a specified mixture of oxygen and helium, capable of supporting human life under appropriate diving or hyperbaric conditions.	BS 8478
High-pressure liquefied gas	Liquefied gas, which has a critical temperature between -50°C and +65ºC	ISO 10286
Incident (Accident)	See definition for Accident	JSP 375
Industrial gas	Gas which is used in a technical process in industrial production or similar activity	ISO 10286
Inert gas	Gas which does not readily react chemically with other substances	ISO 10286
Inhabited Building	A building or structure occupied in whole or in part by people.
Inside Quantity Distance	See definition of ‘Quantity Distance’.	JSP 482
Intrinsically Safe	An intrinsically safe circuit is one in which any electrical sparking that may occur in the normal working, under the conditions specified by the certifying authority and with the prescribed components, is incapable of causing an ignition of the prescribed flammable gas or vapour. / An intrinsically safe apparatus is one which is protected based on the restriction of electrical energy within equipment and of interconnecting wiring exposed to the explosive atmosphere to a level below that which can cause ignition by either sparking or heating effects. / Notes: / 1. The use of the term intrinsically safe in normal working is intended to cover sparking that may in normal use be produced by breaking line current or a short circuit across the lines in the circuit that is required to be intrinsically safe. It is also intended to cover sparking that may be produced under any conditions of fault, which in the opinion of the certifying authority might arise in practice. / 2. The certifying authority referred to in the above is the Department of Trade and Industry.	BS EN 60079-11
Liquid Transfer Area	An area adjacent to the tank, which surrounds the tanker, when the latter is in the filling/discharge position, and which includes the access apron.	BCGA CP 36
Liquefied Gases	Gas, which, when packaged for transport, is partially liquid (or solid) at some temperature above –50ºC	ISO 10286
LPG	LPG is the abbreviation used to describe ‘Liquefied Petroleum Gas’. The name describes a group of hydrocarbon gases which exist as vapour under ambient conditions of temperature and pressure, but which can be liquefied by the application of moderate pressure and/or refrigeration. / Note: LPG is normally marketed as commercial butane (C4H10) or commercial propane (C3H8).
LPG Authority	An authority, normally the DIO or appointed person by them, having specialist knowledge concerning the storage and handling of LPG.
Lower Explosive Limit (LEL)	This is synonymous with ‘lower flammable limit’. It is the minimum concentration of vapour in air or oxygen below which propagation of flame does not occur with a source of ignition.
Low-pressure liquefied gas	Liquefied gas, which has a critical temperature equal to or above +65ºC.	ISO 10286
Maximum permissible operating pressure	Highest pressure permitted to be developed during service.	ISO 10286
Maximum Liquid Level Device	A bleed valve connected to a dip tube terminating at the maximum permitted filling level in a vessel to indicate its maximum permitted level when being filled.
Maximum permissible filling weight	Product of the water capacity of the cylinder and the filling ratio of the gas.
Medical gas	Gas intended to be administered to patients for therapeutic, diagnostic or prophylactic purposes, or to be used for surgical tool applications.	ISO 10286
Minimum Pressure	The pressure below which a cylinder is not to be discharged in normal use.
Multiple Element Gas Container	Multi-Element Gas Container (MEGC) is a unit containing elements which are linked to each other by a manifold and mounted on a frame. The following elements are considered to be elements of a MEGC: cylinders, tubes, pressure drums and bundles of cylinders as well as tanks for the carriage of Class 2 having a capacity of more than 450 litres. MEGC also known as Manifold Cyl Pack (MCP).	ADR
Naked Lights	The term naked lights is to include all exposed flames, incandescent materials, lamps (e.g. torches, electric lights, hurricane lamps) of an unapproved pattern, gas and electric welding and portable hand or power operated equipment of an unapproved pattern.
Nitrox	A gas comprising a specified mixture of oxygen and nitrogen, capable of supporting human life under appropriate diving or hyperbaric conditions. / Note: This includes manufactured gas mixtures made up from combinations of pure oxygen and pure nitrogen, with or without compressed air.	EN 12021
Nominally empty container	A container from which most if not all liquid has been discharged but which will still contain LPG vapour.
Nominal pressure	In accordance with common international understanding, the working pressure.	ISO 10286
Numerical coding	A system of identifying by a 4-digit numerical code the properties of a gas/gas mixture with respect to fire potential, toxicity, physical state and corrosiveness.
Operating pressure	Varying pressure which is developed in a cylinder during service	ISO 10286
Outside Quantity Distance	See definition of ‘Quantity Distance’.	DSA 03 OME Part 2
Oxidising gases	Gases which in the presence of combustible materials can be ignited and which promote or are essential for maintenance of combustion.
Pallet	Device for handling several cylinders at the same time.	(BS) EN 1920
Partition	A fire-proof dividing wall, minimum 300 mm, carried from floor to roof without a gap.
Permanent gases	Gases which cannot be liquefied by the application of pressure at temperatures above 10°C.
Personal Protective Equipment (PPE)	Personal Protective Equipment refers to all equipment and products designed to be worn or held by a person at work to protect them against one or more risks to their health and safety.
Pi Mark	A special Logo used on Transportable Pressure Equipment. A mandatory European compliance mark, signifying compliance with the, EC, Pressure Equipment Directive and ADR.
Pigtail	A connecting pipe, usually flexible, between the cylinder valve and the fixed gas piping or installation.
Portable Container	A gas or LPG cylinder not exceeding 150 litre water capacity.
Preparation	A mixture or a solution of two or more substances.	CHIP Regulation, REACH Regulation
Pressure	Pressures used in this document are gauge pressures, except where otherwise stated.
Pressure receptacle	A collective term that includes gas cylinders, tubes, pressure drums, closed cryogenic receptacles and bundles of cylinders.	ADR
Pressure Regulator	A pressure regulator is fitted to the outlet of the gas cylinder valve and reduces the pressure of the gas from the cylinder pressure to the lower pressure required for the operation of the process equipment.
Pressure relief device	A device which is fitted to the cylinder or its valve and designed to open to prevent a rise of pressure in excess of a specified value because of excess temperature and/or pressure.	(BS) EN 1919
Pressure Relief Valve	A valve of specified performance designed to relieve pressure within a pressure container above the design pressure.
Pressure Stage	An area of the installation defined by the upstream and downstream equipment. / High: That part between the outlet valve of the cylinder/vessel and the inlet of the 1st stage regulator. / Intermediate: That part between the outlet of the 1st and 2nd stage regulators. / Low: That part between the outlet of the 1st stage (or 2nd stage if an intermediate stage is used) and the inlet of the appliance.
Pressure System	A system comprising one or more pressure vessels of rigid construction, including any associated pipework and protective devices, which contains, or is intended to contain, a relevant fluid.	JSP 375
Pressure Vessel	A closed vessel consisting of one or more independent chambers, any of which may be subject to an internal pressure greater than 0.5 bar and is used, or is intended to be used, to contain a relevant fluid.	JSP 375
Propellant gas	Gas under pressure used in a machine or apparatus to create a mechanical force.	ISO 10286
Purge	Definition 1: Vent momentarily, a process which allows the contained gas to blow away any contamination/debris from the gas outlet. / Definition 2: Vent, a process using a gas source to clean and flush out contaminants from inside a container.	BCGA
Quantity Distance	There are two types, Inside and Outside: / Inside Quantity Distance: / Inter-Magazine Distance. The distance between a building or stack containing explosives to other such buildings or stacks which will prevent the direct propagation of explosives or fire from one to the other by missile, flame or blast. / Process Building Distance. The distance from a building or stack containing explosives to a Process Building, or from a Process Building to another Process Building, which will provide a reasonable degree of immunity for the operatives within the Process Building(s), and a high degree of protection against immediate or subsequent propagation of explosions. / Outside Quantity Distance: / Inhabited Building Distance. The minimum permissible distance between a Potential Explosion Site and inhabited buildings, caravan sites, places of assembly, etc, which is such that the ignition or explosion of explosives at a Potential Explosion Site will not cause severe structural damage to those buildings or unduly hazard their occupants, be they Service or civilian. / Public Traffic Route Distance. The minimum permissible distance between a Potential Explosion Site and public traffic routes which is such that the ignition or explosion of explosives at the Potential Explosion Site will not cause intolerable danger to the occupants of vehicles at an Exposed Site.	DSA 03 OME Part 2
Rare gas	Gas which “never” reacts chemically with other substances. / EXAMPLES: Argon, helium, neon, krypton.	ISO 10286
Recovery cylinder	Cylinder provided to recover ‘contaminated’ product for return, normally disposal.
Refrigerant gas	See definition of Cryogenic Liquid	ISO 10286
Refrigerated liquefied gas	Gas which when packaged for transport is partially liquid because of its low temperature	ISO 10286
Relative Humidity (RH)	The ratio of the actual vapour pressure to the saturation vapour pressure over a plane liquid water surface at the same temperature, expressed as a percentage.
Restricted Area	A temporarily defined area, which may or may not be in an existing hazardous area, in which there is increased risk of fire, explosion, asphyxiation, poisoning from fumes or gas, due to spillage, defects in installation, or type of maintenance operation to be carried out.	JSP 375 Vol 3 Chap 5
Respiratory Protective Device (RPD)	Personal Protective Equipment designed to protect the wearer's (3.257) respiratory tract against the inhalation of hazardous atmospheres.	ISO 16972
Safe Area	Any area, no part of which lies within a specified dangerous, restricted or hazardous area.
Safety Area	The area which is covered by the safety distance.
Safety Distance	The distance to be observed with regards to gas and LPG stocks to ensure the minimum practical risk to life and property should an explosion occur.
Safety distance external	The minimum distance between any gas cylinder storage area or bulk cryogenic liquid installation to the nearest main road, private building etc. so as to provide reasonable assurance of safety to life and property.
Safety distance internal	The minimum distance required between storage sub-divisions of flammable, oxidising and inert gas cylinder stacks.
Scientific gas	A gas which is used for analysis, calibration and other similar purposes in scientific laboratories	ISO 10286
Separation distance	The horizontal distance between the nearest container in the storage area and the reference feature.
Settled pressure	Pressure of the contents of a gas cylinder in chemical, thermal and diffusive equilibrium	ISO 10286 / ADR
Source of Ignition	All naked lights or a spark or flame produced by any other means.
Stack	One or more cylinders located together, all containing the same type of gas.
Stamp marking	Permanent markings, applied to the cylinders by hard metal stamping, engraving, casting or other similar methods. In the case of composite cylinders, some permanent markings may be achieved by the use of a printed label, placed in the resin.	BS EN / ISO 13769:2006
Stencilling	Marking of the item using inks and/or paints.	BS EN ISO 13769:2006
Tare weight	The tare weight is the sum of the empty weight plus the mass of any coating (e.g. paint) used in service, the mass of the valve including dip tube where fitted, any fixed valve guard and the mass of all other parts that are permanently attached (e.g. by clamping or bolted fixing) to the cylinder.	BS EN ISO 13769:2006
Storage Area (or store)	An area set-aside for the storage of Industrial Gases and LPG containers where there is no intention of using the products.
Storage sub-division.	One or more adjacent stacks of cylinders; each stack being composed only of cylinders containing gases of the same principal hazard classification, i.e. flammable, oxidising or inert.
Substance	A chemical element and its compounds in the natural state or obtained by any production process, including any additive necessary to preserve the stability of the product and any impurity deriving from the process used, but excluding any solvent which may be separated without affecting the stability of the substance or changing its composition.	CHIP Regulation, REACH Regulation
Temperate climate	A climate in which the maximum shade temperature does not exceed 35°C; and thus the contents of a container stored in the shade is not likely to exceed 35°C.
Test life expired	A cylinder which has not been pressure tested within the periods laid down.
Test pressure	Required pressure applied during a pressure test for qualification or re-qualification.	ISO 10286
Total weight	Tare weight of the cylinder plus the maximum permissible filling weight.	(BS) EN 1919
Toxic gases	Gases which have a toxic effect when breathed; this includes corrosive gases. / Gases classified as UN Class 2, Hazard Division 2.3	ADR
Transit devices	This term embraces all protective items e.g. rubber grommets, coir covers, cradles required by transport authorities as a condition of acceptance of compressed gas cylinders for transportation.
Trimix	A gas comprising a specified mixture of oxygen, helium and nitrogen, capable of supporting human life under appropriate diving or hyperbaric conditions. / Note: This includes manufactured gas mixtures made up from combinations of pure oxygen, pure helium and pure nitrogen, with or without compressed air.	EN 12021
Tropical climate	A climate in which the maximum shade temperature exceeds 35°C; and thus the contents of a container stored in the shade is likely to exceed 35°C.
Water capacity	A ‘value’ declared by the manufacturer and permanently stamped on the cylinder shoulder. It is the capacity, in units of volume (litre), of the container when it is completely filled with water. It depends upon the dimensions of the container and not the liquid used to fill the container.
Wet gas	A gas in which the water content of the gas is in excess of the gas specification.
Wetting Test	Method used initially to establish if an acetylene cylinder is hot from an internal decomposition caused by a flashback or by exposure to fire. The wetting test may also be subsequently used to indicate if an on-going decomposition is slowing down inside the cylinder and that the external shell has cooled indicating that a spontaneous explosion is unlikely, given on-going cooling.
Working pressure	The Settled pressure of a compressed gas at a uniform reference temperature of 15°C in a full gas cylinder	ISO 10286 / (BS) EN 1920
Valve guard	A device protecting the valve during handling, transportation, storage. It need not be removed to provide access to the valve.	ISO 11117
Valve protection cap	A device securely fixed over the valve during handling, transportation, storage. It is removed for access to the valve.	ISO 11117
Vulnerable Population	People who cannot be evacuated easily and quickly from buildings because of age or infirmity. For example, those in a nursery school, old people’s home hospital or correction centre. It also includes buildings where people sleep.
Yield pressure	Pressure at which the actual yield strength of a cylinder is reached. / Note: Exceeding the yield pressure will cause a permanent increase in the cylinder volume.	ISO 10286

# Annex B - Abbreviations

Description	Abbreviation	Source
A
Agreement Concerning the International Carriage of Dangerous Goods by Road	ADR	ADR
Air Commodities Project Team	AC PT
Air Conditioning and Refrigeration Industry Board	ACRIB
Air Separation Unit	ASU
Air and Space Interoperability Council	ASIC
Air Port of Embarkation	APOE
Air Publication	AP	MOD
Airfield and Bulk Fuels Group	ABFG
Allied Command Europe	ACE
Allied Publication	AP	NATO
Allied Quality Assurance Publication	AQAP	NATO
American, British, Canadian, Australian	ABCA
Amendment List	AL	MOD
As Low As Reasonably Practicable	ALARP
Authorising Engineer	AE
Authorised Person Petroleum	AP (Petroleum)
Aviator’s Breathing Oxygen	ABO	USA terminology
B
Base Level Budget	BLB
Boiling Liquid Expanding, Vapour Explosion	BLEVE
Book of Reference	BR	RN
British Compressed Gases Association	BCGA
British Oxygen Company	BOC
British Standard	BS
British Standards Institute	BSI
C
CE Mark(ing)	CE Mark
Central Branch Commercial – Energy Procurement for Defence	CBC – EPD
Central Health and Safety Project	CHASP	MOD
Chief Environmental Safety Officer	CESO	MOD
Chief of Defence Logistics	CDL	MOD
Chief of Fleet Support	CFS
Clinical & Professional Support Division	CPSD
European Committee for Standardization	CEN
Compliance Monitoring Group Focal Point	CMP
Compressed Natural Breathing Air	CNBA	Def Stan 68-284
Construction Industry Training Board	CITB
Control of Major Accident Hazards	COMAH	HSE
Control of Substances Hazardous to Health	COSHH	HSE
Construction (Design & Management) Regulations	CDM
Defence Infrastructure Fire standards (DIFS)	DIFS
Customer Supplier Agreement	CSA
Cryogenics and Gas Section	CGS
D
Dangerous Substances and Explosive Atmospheres Regulations	DSEAR
Defence Dangerous Goods and Hazardous Stores Group	DDGHSG
Defence Equipment and Support	DE&S
Defence Fuels and Gases Environment and Safety Board	DF&GESB
Defence Fuels Operation Centre	DFOC
Defence Infrastructure Organisation	DIO
Defence Standard	Def Stan
Defence Supply Chain Operations and Movements	DSCOM
Defence Support Group	DSG
Defence Training Estate	DTE
Defence Works Advisor	DWA
Department for Transport (UK)	DfT
Department of Transportation (USA)	DoT
Deployable Support & Test Equipment PT	DS&TE PT
Director Defence Health & Safety	D Def H&S
Director Joint Support Chain	D JSC
Director Supply Chain Operations	Dir SC Ops
E
Environment Agency	EA
Environment, Safety & Training Sub-committee	ES&TSC	DES LCS OLG TEAM
Equipment Sub Committee	ESC	DES LCS OLG TEAM
Equipment Support	ES
Establishment Works Consultant	EWC
Euro Atlantic Partnership Council	EAPC	MOD
European Agreement Concerning the International Carriage of Dangerous Goods by Road	ADR	ADR
European Chemical Agency	ECHA
European Committee for Standardization	CEN
European Community	EC
European Standard (Norm)	EN
European Union	EU
Expeditionary Airfield Facilities	EAF
Expeditionary Logistics Wing	ELW
F
First Aid Fire Appliances	FAFA
Fleet Air Arm	FAA
Fluorinated Gas	F Gas
Fuels & Gas Safety Regulator	FGSR
Focal Point	FP	MOD
Fuels & Lubricants	F&L
Fuels Safety Assurance Assessment	FSAA
Fuels Safety Working Group	FSWG
G
Good Manufacturing Practice	GMP
Government Pipeline and Storage System	GPSS
Ground Support Equipment	GSE
H
Hazard Division	HD	ADR
Head of DFR	Hd DFR
Health & Safety at Work Act	H&SWA
Health & Safety Executive	HSE
Health & Safety Guidance Note	HS(G)	HSE
Higher Explosive Limit	HEL
Higher Level Budget	HLB
HQ Air Command	HQ Air
HQ Land Forces	HQ LF
HQ Land Forces Directorate of Infrastructure	HQ LF D Infra Sp
HQ UK Support Command (Germany)	HQ UKSC(G)
Hydrochlorofluorocarbon(s)	HCFC
I
Inside Quantity Distance	IQD	JSP 482
Institute of Petroleum (Now known as the Energy Institute (EI))	IP
International Air Transport Association	IATA
International Civil Aviation Authority	ICAO
International Maritime Dangerous Goods Code	IMDG Code
International Maritime Organisation	IMO
International Standards Organization	ISO
J
Joint Air Publication	JAP	MOD
Joint Force Logistic Component	JF Log C
Joint Helicopter Command	JHC
Joint Service Publication	JSP	MOD
Joint Support Chain Services	JSCS
K
L
Land Systems Fuels & Lubricants Sub-Committee	LSF&LSC
Liquid Oxygen	LOx
Liquid Nitrogen	LiN
Liquefied Petroleum Gas	LPG
Logistic Support Inspections	LSI
Logistic Support Services	Log Sp Svcs
Logistic Support Technical Inspections	LSTI
Logistic Support	Log Sp
Long Term Costing	LTC
Lower Explosive Limit	LEL
M
Major Accident Control Regulations	MACR	MoD
Maximum Explosive Limit	MEL
Medicines and Healthcare products Regulatory Agency	MHRA
Medical & General Supplies Team	M&GS Team
Military Works Force	MWF
Ministry of Defence	MOD or MoD
MoD Defence Works Functional Standards Safety Rules & Procedures	SRP	MOD
MoD Demand Priority Code - (Stores Priority Code)	SPC
Montreal Protocol	MP
Montreal Protocol Substances Bank	MPSB
Montreal Protocol Task Force	MPTF
Motor Transport Fuelling Installation	MTFI
Multiple-Element Gas Container	MEGC
N
NATO Military Standards and Terminology	NMSt	MoD
NATO Standardisation Agreement	STANAG	NATO
NATO Stock Number	NSN
Nitrogen Concentration Trolley	NCT
Nuclear, Biological and Chemical	NBC
New European Valve Outlet Connector	NEVOC
North Atlantic Treaty Organisation	NATO
Northern Ireland	NI
O
Oil Fuel Depots	OFD
Oil Industry Emergency Committee	OIEC
Operating Authority	OA
Out of Area Operations	OOA Operations
Outside Quantity Distance	OQD	JSP 482
Ozone Depleting Substances	ODS	JSP 418
P
Permanent Joint Headquarters	PJHQ
Personal Protective Equipment	PPE
Personal Role Radio	PRR
Petrol, Oils & Lubricants (Obsolete – Use ‘F&L’)	POL	JSP 317
Pressure Relief Valve	PRV
Pressure Systems Safety Regulations	PSSR	HSE
Products Sub Committee	PSC	DES LCS OLG TEAM
Project Team	PT
Property Manager	PROM
Q
Quality Assurance	QA
Quality Control	QC
Quality Surveillance	QS
R
Rail Tank Cars	RTC
Reichs-Ausschuss für Lieferbedingungen Number	RAL No.
Registration, Evaluation, Authorisation and Restriction of Chemicals	REACH
Regulations concerning the International Carriage of Dangerous Goods by Road	RID
Reporting of Injuries, Diseases and Dangerous Occurrences Regulations	RIDDOR	HSE
Respiratory Protective Device	RPD
Role Office	RO
Royal Air Force	RAF
Royal Engineers	RE
Royal Fleet Auxiliary	RFA
Royal Logistic Corps	RLC
Royal Navy	RN
Royal School of Mechanical Engineering	RSME
S
Safety, Health, Environment & Fire Management Board	SHEFB	MOD
Safety Data Sheet	SDS
Sea Port of Embarkation	SPOE
Secretary of State	S of S
Service Focal Points	SFP
Siting Board	SB
Specialist Petroleum Inspections	SPI
Spillage Report	SPILLREP
Standard Operating Procedure	SOP
Standardisation Agreement (ABCA)	QSTAG
Statement of Requirement	SOR
Statement of User Requirement	SUR
Status of Forces Agreement	SOFA
Statutory Instrument	SI
T
Top Level Budget (Command)	TLB
Training Group Development Agency	TGDA
Transition to War	TTW
U
Unit Identity Number	UIN
United Kingdom	UK
United Kingdom Accreditation Service	UKAS
Liquid Gas UK)
United Nations	UN
V
Vice Chief Defence Staff	VCDS
W
Wet Stock Management	WSM
Working Party	WP
Works Service Manager	WSM

# 1 - Introduction to Gases

Chapter Sponsor - DSFA Technical Gases Manager

## Scope

            1. Accidents involving gas cylinders can cause serious injury or even death. JSP 319 provides practical advice on eliminating or reducing the risks associated with using gas cylinders.

            1. This chapter is written around compressed gases, e.g. gases supplied in pressure receptacles as permanent gases, liquefiable gases or dissolved gases. Much of this chapter, especially legislation, also applies to gases supplied as cryogenic liquids. Refer to Part 2, Chap 12, for more details regarding the specifics of cryogenic liquids.

## General

            1. The legal term that covers gas cylinders is “pressure receptacles”. This is a generic term covering a number of types of pressure receptacle: tube, pressure drum, cryogenic receptacle, bundle of cylinders as well as cylinders themselves, plus the valve(s) fitted directly to the receptacle. For the purpose of this publication, the term “gas cylinder” or “gas receptacles” shall be taken to mean all these various types of pressure receptacles.

            1. Gas cylinders used in adverse or extreme conditions, such as for breathing apparatus, may require special precautions. Although the advice in this publication is valid for all uses of gas cylinders certain special precautions, such as different frequencies for periodic inspections, are not covered and if in doubt advice should be sought from the Support Authority responsible for the use of the equipment in-service.

            1. The MOD has a duty to provide a safe workplace and safe work equipment and to ensure, so far as is reasonably practicable, the health, safety and welfare at work of all its employees. It is the duty of every employee while at work to take reasonable care for the health and safety of themselves and of other persons who may be affected by their acts or omissions at work. Gas cylinders are potentially very dangerous, and consequently they have been designed and manufactured to be as safe as is reasonably practical for use in the workplace. All persons handling and/or using gas cylinders shall maintain the safe practices detailed in this publication and are to be aware of the potential for danger that exists within a cylinder.

            1. Gas Cylinders. All gas cylinders have to be designed and manufactured to an approved standard to withstand everyday use and to prevent danger. They shall be initially inspected before they are put into service to ensure they conform to the approved standard and be periodically examined at appropriate intervals to ensure that they remain safe while in service.

            1. New Equipment. If a new item of equipment is to be introduced into service which will contain a removable transportable gas cylinder, the Support Authority (Project Manager) shall consult with the DSFA Technical Gas Manager to establish whether any current in-service cylinders, or Team LEIDOS Lubes and Gases Inventory Manager for supplied contractor cylinders are suitable for the equipment. Special-To-Type cylinders shall be avoided wherever possible.

            1. All gas cylinders which are required to be transported with a pressure charge shall meet the relevant legislation relating to the carriage of dangerous goods; refer Part 2, Chap 8. This is of particular importance when procuring gas cylinders from abroad.

            1. Storage. When not-in-use or being transported, all gas cylinders shall be kept in an approved gas cylinder store which has been designed specifically for the storage of gas cylinders. Health and safety law require that those responsible for work activities shall ensure that all hazards are identified, risks are adequately assessed, and suitable control measures are put into service. Storage at a particular site shall be based on an understanding of the physical and chemical properties of the substances concerned, as well as the overall quantities and size of individual packages. The storage of any substance requires that a suitable Risk Assessment shall be carried out to determine the potential for the item to cause significant harm or damage.

            1. The potential hazards require that all persons on the storage site shall be adequately trained to ensure that they are aware of the risks of storing dangerous substances and can take the precautions necessary to safely store and handle those dangerous substances.

            1. When in a store, the properties of a substance, how it is stored, and the control of ignition sources are all major factors in determining the likelihood of a fire or explosion incident occurring. All dangerous substances shall be assessed to determine a suitable segregation policy so as to reduce the potential for ignition. Often it is not the dangerous substance that is the first material ignited in a fire. For example, small quantities of dangerous substances stored in a general goods warehouse could significantly increase the severity of a fire. This will consequently increase the danger to any personnel in the area as well as the emergency services.

            1. Gas cylinder stores shall be designed and managed in accordance with Part 2, Chap 9.

            1. Storage of empty cylinders. All gas cylinders shall be stored, handled and treated as a hazardous item, i.e. the same as a full gas cylinder. Exceptionally, if adequate measures have been taken to nullify any hazard within the cylinder, the cylinder may be treated as non-hazardous. It is recommended that these cylinders are still stored in an approved gas cylinder store. However, where such a cylinder is kept in a non-hazardous store, e.g. empty new/refurbished cylinders kept as spares, each cylinder shall be clearly identified as being non-hazardous and shall be certified as such by a competent person.

## Hazards

            1. Hazards of Gas Cylinders. Gas cylinders are a convenient way to transport and store gases under pressure. The main hazards are:

Impact from the blast of a gas cylinder explosion or rapid release of compressed gas.

Impact from parts of gas cylinders or valves that fail, or any flying debris.

Contact with the released toxic or corrosive gases or fluids (such as chlorine).

Fire and/or explosion resulting from the escape of flammable gases or fluids (such as liquefied petroleum gas).

Oxygen-enrichment and increased fire risks from released oxidants, such as oxygen, nitrous oxide and fluorine.

Asphyxiation risks from released inert gases – most gases except air, oxygen and some diving/medical gas mixtures.

Some gases are heavier than air so released gases, and their associated hazards, collect in low areas, such as basements, cellars, cable ducts, drains, etc.

Impact from falling cylinders.

Manual handling injuries.

            1. Crush Hazard. Due to the mass, shape and size of many gas receptacles, most accidents with compressed gas cylinders occur during their handling. Full cylinders of compressed gas can weigh more than 100kg and present a serious crush risk to hands and feet.

            1. Hazards Associated with Pressurised Receptacles and Industrial Gases. The properties of some of the common industrial gases are detailed within Part 2, Chap 1, Annex A.

            1. Pressure. Most gases are supplied compressed in metal or composite receptacles such as cylinders and drums. Whenever the properties of the gas or gas mixture permits, the suppliers generally utilise the maximum pressure potential of the receptacles. Pressures of up to 300 bar are common in the MOD. Some specialist receptacles are higher.

            1. Pressure vessels can fail if over-pressurised or be weakened by exposure to excessive heat. General and localised heating may cause the internal pressure to increase and could, in extreme circumstances, result in a serious failure of the receptacles. Conversely, steel gas cylinders are prone to brittle failure if they become very cold, e.g. by contact with cryogenic liquids. Corrosion or mechanical damage to the receptacles, and especially the valve, could result in a rapid escape of gas which could generate sufficient thrust to propel the gas receptacles or other adjacent objects.

            1. Gas Escape. An uncontrolled release of gas, known as a gas escape, caused by the inadvertent opening or shearing-off of the cylinder valve can present a hazard to people and equipment regardless of the nature of the gas. The released pressure can also turn the cylinder into a powerful projectile.

            1. Pressure Release Devices. Cylinders used for industrial gases are not generally fitted with pressure relief devices. Carbon dioxide cylinders are protected by bursting discs, and some acetylene cylinders are protected by bursting discs or fusible plugs. These devices operate either directly, due to excessive heat applied to the device (e.g. fusible plugs), or indirectly, by the heat raising the pressure in the cylinder (e.g. pressure relief valves or bursting discs). It should be noted that whilst these devices should protect the cylinders from catastrophic failure, their operation may give rise to a localised hazardous atmosphere.

            1. Transportable vacuum-insulated cryogenic gas receptacles are fitted with pressure relief devices which, during normal operation, are designed to lift and vent any excess pressure.

            1. Valve Outlets. There are a variety of different valve outlet connection standards and codes available. Extreme care must be taken to ensure only the correct connectors are used in accordance with the supplier’s recommendations. If there is any doubt as to the suitability of the valve connector, the Support Authority responsible for the cylinder, or the gas supplier, is to be consulted, Refer to BCGA TIS 10 on new cylinder valve outlet connections.

## Hazardous Gas Monitoring

            1. Despite the other precautions taken to minimise the effects of hazardous gas escapes, gas detection equipment shall be installed for specific gases unless it can be demonstrated that the largest foreseeable escape of any particular gas will cause no danger to the health of persons or damage to the environment. Nevertheless, gas monitoring is compulsory for gases which may damage the environment (e.g. 'F' gases or refrigerants) and it is strongly recommended for very toxic gases, oxidants, flammable gases that form explosive mixtures with air and asphyxiates. Monitoring shall be recorded, and records kept for 2 years.

            1. Many gases are heavier (denser) than air, so escaping gases may build up in low lying areas, such as basements, cellars, inspection pits, drains, cable ducts, etc. Such “confined spaces”, are subject to legal controls, and the provision of gas monitoring may require detection at both the “normal” breathing zone of 1.5m and at lower levels.

            1. Gas monitoring is a legal requirement in Confined Spaces. Conversely, hydrogen, a flammable gas, is much lighter than air (less dense) and may form pockets in poorly ventilated roof spaces. In this case, gas monitoring may require detection at both the “normal” breathing zone of 1.5m and at higher levels.

            1. Where asphyxiation or oxygen-enrichment is identified as a potential hazard, consideration shall be given to the installation and use of oxygen monitoring equipment.

            1. Ozone Depleting Substances (ODS), and gases with high Global Warming Potential (GWP) are subject to legal controls and a requirement for proactive management. Monitoring shall be carried out at regular intervals, defined by Regulations, in order to detect for leaks; leaks must be repaired promptly; and leakages must be recorded, and, where necessary, reported to the relevant Environmental Lead/Manager. This leak management may be achievable by leak detection or by cylinder weighing refer to Para 39 of this Chapter - and Part 2, Chap’s 9 and 14).

            1. Outputs from the gas detection system should be available at three levels:

Audible and/or visible alarm to warn personnel to take appropriate emergency or corrective action prior to dangerous concentrations being reached.

Automatic gas supply shut-off (bulk permanent tanks only).

Automatic operation of extraction or ventilation systems.

## Gas Classifications

            1. Specific Gas Hazards. Gases are categorised by their primary hazard in order to minimise risks during transportation and storage; and this can be ascertained by the hazard labels on the gas cylinder, refer to Part 2, Chap 3.

            1. It is beyond the scope of this publication to cover the possible hazards of all gases. The safety data sheet is to be consulted for specific hazards. If there is any doubt concerning gas hazards, contact Team LEIDOS Lubricants and Gases or the gas supplier for guidance before the gas is issued and used, (refer to DLF).

            1. Flammable Gases. When mixed with air, flammable gases can freely propagate a flame. Mixtures of flammable gases with air or other oxidants have the potential to explode. The quantity and degree of confinement of the mixture is amongst the many factors contributing to the severity of an explosion caused by the ignition of a flammable and oxidising gas mixture.

            1. Pyrophoric Gases. Pyrophoric gases may spontaneously ignite and burn in the presence of air and other oxidants. Under some conditions, spontaneous ignition may not occur, resulting in the formation of an unstable pyrophoric and oxidant gas mixture which may subsequently explode.

            1. Oxidising Gases. Oxidising gases support combustion in a manner similar to oxygen and will react with flammable gases and other combustible materials. Some oxidising gases will support combustion more vigorously than air or oxygen and may react spontaneously with some flammable gases and other materials.

            1. Some organic materials such as hydrocarbon-based oils, greases and plastics, may react explosively with oxygen and more powerful oxidants (e.g. fluorine). The severity of such an explosion will depend on pressure, temperature, reactivity and concentration of the reactive components. Metal fires may be initiated in the presence of oxidants and hydrocarbon oils, greases, and other organic contaminants or particulate matter.

            1. Toxic Gases. When inhaled in low quantities, toxic gas can cause acute or chronic damage to health, and prolonged exposure can cause death. Although toxic gas would normally enter the body by inhalation, it may also be ingested or absorbed through the skin.

            1. Corrosive Gases. Human tissue may be harmed if it comes into direct contact with corrosive gas. Many corrosive gases may also react with certain construction materials, possibly causing damage and failure. Some corrosive gases may only react with a material in the presence of moisture. The process of corrosion can include the production of other gases such as hydrogen, giving rise to possible pressure and flammability hazards.

            1. Asphyxiating Gases. A potential asphyxiation hazard exists where any gas or gas mixture does not contain sufficient oxygen to support life. For fit people, the generally accepted minimum safe oxygen level is 19.5%. Asphyxiant gases or gas mixtures can displace the available oxygen in the atmosphere to a level which is unsafe. It should be noted that all gases are asphyxiates except oxygen, air, and gas mixtures manufactured specifically for breathing at atmospheric pressure. Many asphyxiating gases may well present other hazards such as fire or toxicity risks. The concentrations at which these other hazards can arise are likely to be well below those at which asphyxiation occurs.

            1. Other Gas Classifications. There are a few gases which are carcinogenic, mutagenic and teratogenic. Where this is the case, information shall be provided by the supplier's safety data sheet and indicated on the gas receptacles supply label. Where practicable, gases with such severe hazards should be substituted for less hazardous ones.

## Hazards to the Environment

            1. Substances with the potential to cause environmental pollution (prescribed substances), are those substances or classes of substances whose release into the environment is prescribed in Part I of the Environmental Protection Act 1990. They are listed in the Environmental Protection (Prescribed Processes and Substances) Regulations 1991 (as amended), and cover releases to the environmental media of air, water and land. Care shall be taken whenever gases are released to the atmosphere. The need for MOD sites to discharge waste gases to the atmosphere has been greatly reduced by the conditions of the direct supply contract the MOD has with its contractor. However, if the operational situation requires the discharge of waste gases, the table at Annex B to this Chapter shall be followed. Discharges shall be recorded and reported to the relevant Environmental Lead/Manager; all discharges above 25 kg shall be reported by the Environmental Lead/Manager to the TLB Safety Organisation (refer to Part 2, Chap 14).

            1. The Montreal Protocol came into force on 1 January 1989 and is intended to phase-out, by the year 2020, the use of chemicals known to be responsible for depleting the ozone layer. Certain aspects of the EC Regulation 3093/94, which formalised the agreements at Montreal, were implemented in the UK by the Environmental Protection (Controls on Substances that Deplete the Ozone Layer) Regulations 1996. However, some gaseous Montreal Protocol substances for which there are no suitable alternative currently available, are held and managed centrally on behalf of the DSFA. Further information is available in JSP 418 - Management of Environmental Protection in Defence.

            1. Concern over climate change has led to International Conventions, such as the Kyoto Protocol, and various European Union legislation, on certain fluorinated greenhouse gases, (‘f’ gases). This has led to controls on certain classes of fluorinated gases, i.e. hydrofluorocarbons (HFCs), Perfluorocarbons (PFCs) and sulphur hexafluoride (SF6), with high Global Warming Potential (GWP); and targets for their reduction and replacement. MOD users are required to annually report their holdings, estimated discharges to atmosphere, measures taken to minimise emissions to atmosphere and progress being made on their replacement (see JSP 418 , Vol 2, Leaflets 5-8).

            1. Refrigerants and sulphur hexafluoride are classed as Hazardous Waste and are subject to the current Hazardous Waste Regulations. They shall not be discharged or given to contractors, but shall be recovered into recovery cylinders and arrangements made for Team LEIDOS Lubricants and Gases contractor to collect them (refer to Part 2, Chap14).

            1. The UK Government has introduced mandatory minimum qualifications for handlers of Ozone Depleting Substances. They specify minimum qualifications for personnel handling refrigerants and halons for use in refrigeration and air-conditioning systems, and its recycling, reclamation or destruction. This requirement came into force on 10 July 2006, with all existing workers to be qualified by 09th April 2007 (see JSP 418 Vol 2, Leaflets 5-8).

## Health and Safety

            1. The main causes of accidents are:

  1. Inadequate training and supervision.

  1. Poor installation.

  1. Poor examination and maintenance.

  1. Faulty equipment and / or design (e.g. badly fitted valves and regulators).

  1. Poor handling.

  1. Poor storage.

  1. Inadequately ventilated working conditions.

  1. Incorrect filling procedures.

  1. Hidden damage.

            1. How to reduce the risks. All gas cylinders have to be designed and manufactured to an approved standard to withstand everyday use and to prevent danger. They must be initially inspected before they are put into service to ensure they conform to the approved standard and be periodically examined at appropriate intervals to ensure that they remain safe while in service. If ever a gas cylinder is considered to be unserviceable, or the contents of the cylinder cannot be accurately identified, it is to be made safe by a competent person, returned as unserviceable and a serviceable cylinder obtained as required.

            1. Training. Anyone who examines, refurbishes, fills or uses a gas cylinder should be suitably trained and have the necessary skills to carry out their job safely. They should understand the risks associated with the gas cylinder and its contents. Recognised certified training is also mandatory for handlers of refrigerants and halons for use in refrigeration and air-conditioning systems, and it’s recycling, reclamation or destruction refer to (Part 2, Chap 14).

            1. Health and Safety Awareness. All personnel are to be made aware of their responsibilities when working with pressure equipment, whether transportable pressure vessels or fixed pressure systems. Line management are to ensure that they have implemented the requirements of the Health and Safety at Work Act and that they operate safe working procedures as defined within JSP 375 and where appropriate, the applicable chapters within JSP 375 Vol 1 Chap 29.

            1. Site managers are to have a working knowledge of the Health and Safety at Work, etc Act 1974, and Control of Substances Hazardous to Health Regulations 2002. As a minimum standard, all personnel working with portable gas receptacles are to have a thorough knowledge of:

Safety regulations detailed in this document and all policies, procedures and operation/work instructions for the sites on which they are authorised to work.

Safety Data Sheets for the gases they are likely to be involved with.

Safe handling of gas receptacles.

Identification and hazards of gas receptacles contents.

Gas properties (physical, chemical, hazardous).

Potential hazards of high-pressure receptacles.

Procedure for the supply and disposal of gases, and associated activities.

Personal Protective Equipment (selection, location and use).

Emergency equipment (location and use).

Emergency procedures (gas leaks, fire, etc).

Gas receptacles safety checks on receipt and before return to supplier.

Designated smoking and no-smoking areas.

            1. Operating Procedures. Written Standard Operating Procedures (SOPs) shall be available and understood by all personnel. The accepted SOPs for the safe handling of gases and associated equipment shall be clearly detailed. SOPs shall be prepared by a competent person, issued formally, regularly updated, and reviewed annually. A system of control shall be employed to ensure that only the most recent issue of SOPs and any associated drawings/diagrams are in use; all superseded documents shall be destroyed. New equipment and modifications shall not be put into use until SOPs and drawings/diagrams have been issued or revised appropriately.

            1. Risk Assessments. Sites holding gas cylinders are required by various health and safety regulations to assess risks; provide means of risk prevention and control; and to reduce the risks to levels that are as low as are reasonably practicable (ALARP). The requirements involve the provision of information to employees; ensuring that they are adequately trained; are competent for the tasks they are required to perform; and the provision of periodic refresher training (refer to JSP 319 -Training; Part 2, Chap 1 – Introduction to Gases; and, Part 2, Chap 18 – Liquefied Petroleum Gas Cylinders)

            1. The scope of the arrangements needed to comply with all the applicable regulations may vary from site to site, but compliance will be required with:

Management of Health and Safety at Work Regulations, 1999.

Manual Handling Regulations, 1992.

Control of Substances Hazardous to Health Regulations, 2002 (as amended) (COSHH).

Dangerous Substances and Explosive Atmospheres Regulations, 2002 (DSEAR).

Confined Space Regulations, 1997.

The Registration, Evaluation, Authorisation and Restriction of Chemicals Regulations, 2006 (REACH).

            1. MOD policy on the implementation of these, and other applicable regulations, is detailed within JSP 375.

            1. Internal Auditing. Regular internal audits of gas cylinder compounds, bulk LPG installations and bulk cryogenic storage installations shall be conducted and recorded. They are to be conducted at least twice a year and may be integrated into a general auditing schedule. In particular, audits shall check that:

All operations are covered by authorised SOPs.

Latest issue of all SOPs and drawings/diagrams are readily available.

SOPs are being followed.

Unauthorised modifications have not been made to systems and procedures.

All personnel are adequately trained.

All specified safety and emergency equipment is available and in good condition.

Where Ozone Depleting Substances and/or F-gases are held, they are proactively managed in accordance with JSP 418 Vol 2, Leaflets 5, 6 and 7 and Part 2, Chap 10, as appropriate.

Unwanted part used cylinders of refrigerants and sulphur hexafluoride gas and mixtures are disposed in accordance the current Hazardous Waste Regulations. Unwanted, used product is to be recovered in accordance with MOD Policy (refer to Part 2, Chap 14 ) and disposed of as Hazardous waste gases, as above.

            1. External Auditing. Dangerous Goods compliance audits on transport associated activities will be undertaken periodically by the Defence Goods and Hazardous Stores Group. External auditing of gas cylinder compounds, bulk LPG installations, and bulk cryogenic storage installations shall be carried out by DSA FGSR, refer to DSA 02 & DSA 03.

            1. Major Accident Control Regulations (MACR). Sites which hold large quantities of gaseous products may require qualifying under JSP 498 (MACR). Individual sites may already be qualified under JSP 498 due to their holdings of other substances, such as explosives or bulk fuel storage. Storage of 5 tonnes of hydrogen, 5 tonnes of acetylene, 50 tonnes of LPG, or 200 tonnes of oxygen, for example, will qualify a site at the Lower Tier Threshold (see JSP 498, Chapter 1, Appendices 1A1 and 1A2 for further details).

            1. A fire involving a gas cylinder(s) may have incident reporting implications for MACR qualified sites (see JSP 498, Chapter 1).

## British Compressed Gases Association - BCGA

            1. The British Compressed Gases Association (BCGA) is the British trade association representing companies in the industrial gases industry that manufacture and distribute gases, manufacture receptacles to contain them or equipment to use them. The BCGA seeks to promote safe practice in the manufacture, distribution, storage and use of compressed and liquefied gases.

            1. BCGA publishes Codes of Practice and Guidance Notes that provide guidance on safe practice on the handling and use of gases. They are accepted as industry standards and are recognised as such by the regulatory authorities. Many of these are referenced in JSP 319. Contact details:

4a Mallard Way
Pride Park
Derby
DE24 8GX

Web: www.bcga.co.uk

## Bibliography

            1. Environmental Protection Act, 1990.

            1. Health and Safety at Work, etc, Act, 1974.

            1. Environmental Protection (Controls on Substances that Deplete the Ozone Layer) Regulations, 1996.

            1. Environmental Protection (Prescribed Processes and Substances) Regulations, 1991.

            1. The Hazardous Waste (England and Wales) Amendment Regulations, 2009. No. 507.

            1. The Special Waste Amendment (Scotland) Regulations, 2004. No.112.

            1. Ozone Depleting Substances (Qualifications) Regulations, 2006.

            1. Control of Substances Hazardous to Health Regulations, 2002, (COSHH).

            1. Dangerous Substances and Explosive Atmospheres Regulations, 2002, (DSEAR).

            1. Management of Health and Safety at Work Regulations, 1999.

            1. BCGA CP41 The design, construction, maintenance and operation of filling stations dispensing gaseous fuels.

            1. BCGA CP44 The storage of gas cylinders.

            1. BCGA CP 34 The application of the Pressure Equipment Regulations to customer sites
            2. BCGA CP 18 The Safe Storage, Handling and use of special gases.

            1. Carriage of Dangerous Goods Regulations 2011.

            1. Confined Spaces Regulations 1997 Reg 4.

# Annex A - Properties of Industrial Gases

            1. The main characteristics of commonly used compressed gases are described below.

            1. With the exception of breathing air and oxygen, all gases in sufficient concentrations will asphyxiate without warning.

            1. Safety Data Sheets are available for all gases; and are to be referred to. The safety data sheet will be issued with the gas cylinder. The safety data sheet shall always be considered the authoritative reference for gas characteristics.

Table 1.A.1 - Properties of Acetylene
Gas Type	Properties
Acetylene:	Colourless.
	Odour similar to garlic.
	Non-toxic
	Flammable and will ignite from a spark or by contact with hot metal.
	Lighter than air density 0.9.
	Asphyxiates by depleting oxygen
	Explosive range in air: 2% to 82%.
	Explosive range in oxygen: 2% to 92%

            1. Acetylene gas poses an additional hazard to other flammable gases as it is also reactive. Under certain conditions, even in the absence of any air or oxygen, it can decompose explosively into its constituent elements, carbon and hydrogen. This hazard is not fully addressed by DSEAR and so additional legal requirements for the safe use of acetylene gas at equal to or greater than 0.62bar (“compressed acetylene gas”) and the equipment used with this are provided by the ASR 2014 which came into force on 1 October 2014 to consolidate and modernise existing legislation (refer to Part 1, Chap 5).

            1. Acetylene is produced by the action of calcium carbide in water. The acetylene gas produced is the most powerful and versatile of all the fuel gases which are commercially available. Its chemical formula is C2H2.

WARNING: Overheating may cause decomposition.

            1. Some acetylene cylinders are fitted with bursting discs. These are set to operate at 30.6bar.

            1. Acetylene cylinders are not hollow. They contain a porous material which is impregnated with acetone. Acetone can dissolve 24 times its own weight of acetylene.

            1. It is because of the presence of acetone that the cylinder is to be stood upright when in use. If the cylinder is laid on its side for a period, the acetone will drain towards the cylinder valve and the mixture of acetone and acetylene will come out of the cylinder when the valve is opened.

            1. WARNING: If an acetylene cylinder has been laid on its side then it is to be stood upright for a minimum period of 1 hour before any attempt is made to use it.

            1. WARNING: Overheating may cause decomposition giving rise to high temperatures and possible detonation, even in the absence of oxygen.

            1. WARNING: Acetylene will react with copper, particularly in damp conditions to form copper acetylide. This is an impact explosive. It is for this reason that acetylene should not be allowed to remain in contact with pure copper or brass which contains more than 70% copper. Care is to be taken when selecting components for use in an acetylene system. Many components, e.g. pressure gauges (which traditionally utilise copper in the manufacture of bourdon tubes), have to be specifically designed for use with acetylene.

Table 1.A.2 - Properties of Industrial Gases
Gas Type	Properties
Carbon Dioxide	Colourless.
	Slightly pungent odour in high concentrations.
	Toxic.
	Heavier than air.
	Asphyxiates by depleting oxygen but is also toxic once the concentration reaches several percent by volume.
	Consideration must be given to the dangers of storage and use in confined spaces.
Hydrogen	Colourless.
	Odourless.
	Non-toxic.
	Flammable and will ignite from a spark or by contact with hot metal.
	Lighter than air.
	Asphyxiates by depleting oxygen.
	Burns with a pale blue flame, which can be difficult to see.
	Gas may spontaneously ignite.
	A concentration of as little as 4% in air can burn.
	Considered a fire and explosion hazard.
Inert Gases (Argon, Nitrogen, Helium, etc)	Colourless.
	Odourless.
	Non-toxic.
	Can be lighter (e.g. helium) or heavier (e.g. argon) than air.
	Asphyxiates by depleting oxygen.
	Chemically inert.
	Consideration must be given to the dangers of storage and use in confined spaces.
Methane	Colourless.
	Non-toxic.
	Flammable and will ignite from a spark or from contact with hot metal.
	Lighter than air.
	Asphyxiates by depleting oxygen.
	Must be considered as a potential fire and explosion hazard.
Nitrous Oxide	Colourless.
	Odourless.
	Non-toxic.
	Vigorously supports combustion
	Heavier than air.
	Asphyxiates by depleting oxygen.
	Oils, greases, and solvents may react violently with nitrous oxide.
Oxygen	Colourless.
	Odourless.
	Non-toxic.
	Non-flammable
	Oils, greases and solvents may react violently with oxygen and metals may also burn
	Many materials that would not normally burn in air will readily burn in an oxygen rich atmosphere

            1. For Cryogenic Liquids, refer to Part 2, Chap’s 11 and 12.

            1. For LPG, refer to Part 2, Chap 17,18,19.

            1. For Refrigerants, refer to Part 2, Chap 14.

Table 1.A.3 - Properties of LPG
Property	Commercial Butane	Commercial Propane
Relative Density of liquid at 15°C	0.57 to 0.58	0.50 to 0.51
Litres per Tonne at 15°C	1723 to 1760	1965 to 2019
Relative density to air at 15°C and 1015.9mbar	1.90 to 2.10	1.40 to 1.55
Approximate Boiling Point at 1015.9 mbar (°C)	- 2	- 45
Vapour pressure at 15°C (bar g)	1.93	6.9
Flammability limits, Lower: Upper	1.8: 9.0	2.2: 10.0
Latent heat of Vaporisation (kJ/kg at 15°C)	372.2	358.2
Gross Calorific Value (Btu/ft3)	3270	2500
Notes: / 1. LPG is a petroleum product. It is classified as Class 0 under the Energy Institute's IP 15 Model Code of Safe Practice (Part 15, Area Classification code for installations handling flammable fluids). / 2. For transportation purposes, LPG is classified under the Carriage of Dangerous Goods legislation as Class 2, Division 2.1, Flammable Gas. / 3. LPG is procured against the specification detailed in BS 4250, Specification for commercial butane or commercial propane. / 4. Automotive LPG is procured against BS EN 589.

# Annex B - Waste Gas Discharge to Atmosphere

Serial	Hazardous Property	Principles
1	Toxic and Very Toxic	Routine: / Discharge via appropriate abatement equipment; the efficiency of such equipment must be monitored while in use.
2	Toxic and Very Toxic	Non-Routine: / Consider means of treating, controlling and discharging. If discharging to atmosphere, ensure that it is away from populated areas and air intakes, and diluted with air to ensure personnel are not exposed to concentrated levels.
3	Flammable Gases	All Disposal Operations: / Avoid risk of explosive gas and air mixtures in storage areas. Ensure that there are no ignition sources where there is a risk of flammable gas release. If discharged directly to atmosphere, ensure that it is away from populated areas and air intakes. Flash-back arrestors are to be fitted.
4	Oxygen	All Disposal Operations: / Minimise the risk of fire by avoiding the creation of an oxygen enriched atmosphere.
5	Asphyxiant Gases	All Disposal Operations: / Minimise the risk of creating an asphyxiant hazard by avoiding atmospheric oxygen depletion.

# 2 - Personal Protective Equipment (PPE)

Chapter Sponsor - Not supported, Information Only

## Scope

            1. This chapter details the general requirement for the use of Personal Protective Equipment when handling or using gases, gas cylinders and/or cryogenic liquids, and lists specific Personal Protective Equipment to be used.

## General

            1. Personal Protective Equipment (PPE) refers to all equipment and products designed to be worn or held by a person at work to protect them against one or more risks to their health and safety.

            1. Requirement. The use of PPE is always to be subject to a documented risk assessment. The procedure for carrying out a risk assessment is detailed in JSP 375 . In this context, PPE shall be selected and provided with regard to the particular potential hazards to personnel involved in handling, supply and disposal of cryogenic liquids, liquefied gases, gas and gas receptacles in accordance with the requirements of SI 2002, No.2667 (the Control of Substances Hazardous to Health Regulations, 2002). Risk Assessors are to make reference to the relevant equipment publications, manufacturers’ information and the Safety Data Sheet (SDS). As part of the Risk Assessment, a PPE Assessment shall be carried out (see JSP 375).

            1. The majority of PPE provided by the MOD is detailed in Defence Clothing Catalogue
Reference should be made to this document to identify suitable products that provide the characteristics identified by the PPE assessment.

            1. All PPE worn or held by a person at work to protect them against risks to health and safety should have affirmation of conformity with health, safety, and environmental protection standards. If the product was placed on the market
before 1 January 2021, it must have a ‘CE’ mark.
after 1 January 2021, it must have a ‘CE’ or ‘UKAC’ mark; and
after 1 January 2022, it must have a ‘UKAC’ mark.

            1. Line Managers shall ensure that:

Where a requirement for PPE is specified as part of a documented risk assessment, that a further assessment is made to determine the most suitable PPE for a particular application; and, if the circumstances demand, the person who will use it.

PPE is provided and is worn.

Adequate information, instruction and training is provided and that personnel fully understand the rationale for using PPE.

            1. All person’s handling / operating gas cylinders or cryogenic liquids shall:

  1. Use any PPE supplied to them in accordance with the training or instruction received.

  1. Check PPE serviceability immediately prior to use and report immediately to their Line Manager any loss or defect in the PPE provided to them.

            1. In certain locations, or site conditions, additional protective clothing / PPE may be obligatory, e.g., hard hats, ear defenders and/or breathing apparatus, and that this may introduce PPE compatibility problems which could force an additional risk assessment and the provision of alternative styles of PPE.

            1. All PPE shall be stored in clearly marked locations that are away from areas likely to become contaminated; and shall be decontaminated after use, before being returned to the designated storage location. Where appropriate, equipment (such as self-contained breathing apparatus) shall be stored in receptacles and in the manner recommended by the supplier.

            1. Maintenance of PPE. To ensure that it is kept in good functional condition, all PPE shall be inspected regularly in accordance with local orders and/or the authorised engineering inspection and maintenance schedules.

            1. Unserviceable PPE. Adequate PPE shall be available to replace equipment removed for maintenance or repair. Any unserviceable PPE shall be clearly labelled and stored separately from serviceable equipment. Specific written procedures shall be produced to ensure that unserviceable PPE cannot be used inadvertently.

            1. Breathing Apparatus. All wearers of Respiratory Protective Devices (RPD) shall be trained in its use and retraining / refresher training provided at suitable intervals. The nature of the atmosphere and the working environment will determine the protection required. Equipment used must be to the relevant BS EN standards.

            1. All self-contained breathing apparatus shall be regularly cleaned and checked to ensure their correct operation and that air receptacles (including spare air receptacles) are fully charged; and the checks recorded. Such maintenance shall be carried out each time the equipment is used; and the maintenance recorded. If an in-house air receptacle charging facility is available, it shall be regularly maintained in accordance with the manufacturer's instructions.

            1. Barrier cream. The use of skin barrier creams is undesirable when working with oxygen or oxygen equipment as such creams are often hydrocarbon-based. Their use may lead to the contamination of oxygen equipment and they represent an increased fire hazard to personnel. Users / maintainers are to wear approved clean gloves.

            1. For similar reasons, the use of thin gloves, or latex gloves, that are internally “dusted” with talc, or other powder, is undesirable when working with high pressure oxygen and their use should be subject to an appropriate risk assessment.

            1. Gas monitoring. If working in an environment where there is the potential for gas leaks, consideration should be given to using the following monitoring equipment:

Portable toxic gas monitor.

Portable oxygen enrichment/depletion monitor.

1. Portable flammable gas monitor.
2. Positive pressure breathing apparatus.

            1. Some gases are heavier than air and may collect in low lying areas and/or basement areas, displacing ambient air, leading to either increased asphyxiation or fire risks (refer to, Part 2, Chap’s 9 and 10). Such areas may fall within the scope of the Confined Space Regulations and personnel shall not enter such areas without having complied fully with the requirements of this legislation (refer to Confined Space Regulations and JSP 375).

            1. Portable monitors should be used to compliment permanent monitoring systems in fixed installations (refer to, Part 2, Chap’s 9 and 10). Portable monitors shall be calibrated and checked regularly in accordance with the manufacturer's instructions.

            1. Electrical discharges. PPE intended for use in potentially explosive atmospheres, such as those encountered around flammable and oxidant gas storage vessels, shall be designed and manufactured so that they cannot be the source of an electric, electrostatic or impact-induced arc or spark likely to cause an explosive mixture to ignite. In particular, the selection of footwear, gloves and high-visibility clothing shall be assessed for compliance with the appropriate standards.

## Specified PPE

            1. Emergency Use PPE. Gases produce many hazards. The risk assessment shall highlight the hazards that are likely and where there are increased risks. Where there is an increased risk, provision shall be made to provide PPE specifically for use in an emergency situation. This may include:

  1. Self-contained positive pressure breathing equipment.

  1. Face shield.

  1. Chemically resistant gauntlets/gloves.

  1. Chemically resistant apron or overalls.

  1. Complete body protection suit (for area contaminated with corrosive gas).

            1. The documented risk assessment shall also pre-identify measures to protect the health and safety of personnel entering these areas, such safety harnesses and the provision of standby personnel kitted out with Emergency Use PPE located outside the hazardous area.

Table 2.1 - PPE for use when handling / operating gas cylinders
Body area	Protection required
Hands	Heavy duty industrial gloves. (BS EN 388).
Feet	Wear safety boots or shoes (BS EN ISO 20345) when handling cylinders. The impact resistant toe-caps shall be internal. No steel tips (hob-nails) on sole or heel. Anti-static sole. Metatarsal (midsole) protection recommended.
Eyes		Safety glasses are to be used when connecting or disconnecting gas cylinders. Use chemical goggles or face shield when handling the product in liquid form. (BS EN 166).
Clothing		Wear Coverall FR with long sleeves to cover exposed skin. (BS EN ISO 11612). Keep clean, maintained free from oil & grease. Secure at wrist. Not too loose.
Respiratory		RPD shall be used if there is a risk of high vapour concentration.

            1. PPE for use when handling Liquefied Petroleum Gas (LPG). PPE is always to be used when handling LPG, whether in bulk or packed (cylinders) form, as well as by personnel working in filling plants to minimise the risk of injury / accident.

Table 2.2 - PPE for use when handling / operating LPG
Body area	Protection required
Hands	Use heavy duty industrial gloves when handling cylinders, (BS EN 388). Use rubber (neoprene) gloves if in contact with liquid, (BS EN ISO 374-1). During the transfer / filling of LPG, gloves to resist cold burns are to be worn. (BS EN 511).
Feet	Wear safety boots or shoes (BS EN ISO 20345) when handling cylinders. The impact resistant toe-caps shall be internal. No steel tips (hob-nails) on sole or heel. Anti-static sole. Metatarsal (midsole) protection recommended.
Eyes	Safety glasses are to be used when connecting or disconnecting gas cylinders. Use chemical goggles or face shield when handling the product in liquid form.
Clothing	Wear Coveralls FR with long sleeves to cover exposed skin, (BS EN ISO 11612). Keep clean, maintained free from oil & grease. Secure at wrist. Not too loose.
Respiratory	RPD shall be used if there is a risk of high vapour concentration.

            1. PPE for use when using oxy-fuel gas equipment. Eye protection is essential at all times. It is necessary to protect against heat, glare and flying sparks. Goggles shall comply with BS EN 175 and lenses with BS EN 169.

            1. The outer lens shall be replaced before any build-up of welding splatter, dirt or scratches impede the operator’s vision. Recommendations on the correct shade of filter lens to use are found in BS EN 169. A backing lens should be used if the filter lens is not robust in accordance with BS EN 169. Suitable clothing preferably made from flame-retardant (FR) material should be worn (BS EN ISO 11611). Suitable leather gloves or gauntlets (BS EN 12477) should be worn during operations or when handling metal.

            1. PPE for use when handling Cryogenic Liquids. Many so-called non-flammable textile materials will burn fiercely in air containing as little as 30% oxygen, and no material should be considered totally safe. Fabrics such as nylon should not be worn as these can increase the severity of burns in a fire situation.

            1. Clothes should be well fitting, yet easy to remove. All clothing shall be maintained clean and free from oil and grease. To minimise the risk associated with working in this environment outer clothing needs to be waterproof. Cryogenic liquid will run off in a similar fashion to water. There should be no open pockets or turn-ups where liquid can collect. All pockets require storm flaps. The hood, if fitted, must be stowable. Cuffs should be double layered to prevent the ingress of liquid. Gloves secured over the inner layer. Aprons are not recommended as they may trap liquid between the apron and inner clothing. Water-resistant outer clothing, manufactured from a material with close-formed fabric, such as Gortex™, is recommended.

            1. Items which have the potential to cause a spark are forbidden in close proximity to cryogenic liquids. This includes Personal Electronic Devices, such as cameras, computers, radios and mobile phones, as well as matches, cigarette lighters, smoking materials, etc. These shall not be carried on the person or placed in the pockets of any protective clothing.

            1. Personnel who are required to work in a cryogenic workshop or storage area shall use a set of dedicated clothing and other PPE, so as to maintain it in a ‘clean’ condition and shall be maintained clean and free from oil or grease; and only be used in an Oxygen Bay environment. Such clothing / PPE shall be marked for ‘oxygen bay use only”.

            1. Persons who have been exposed to an oxygen-enriched atmosphere shall not smoke or go near hot spots or sparks until they have properly ventilated their clothes in a normal atmosphere. A minimum ventilation period of 15 minutes, with movement of the arms and legs, and with the outer clothing loosened, may be necessary.

            1. Barrier Creams. The use of skin barrier creams is undesirable as such creams are often hydrocarbon based. Using barrier cream may lead to contamination of oxygen equipment and may present an increased fire or explosion hazard.

            1. Approved gloves (minimum specification BS EN 511) are essential to protect the hands when handling valves or metal parts through which a cryogenic liquid flow. Gloves should be a loose fit so that they may be readily removed should liquid splash onto them or into them; or in case of “freezing” onto cold metal parts. Gloves should incorporate an elasticated knitted wrist.

            1. Only a single layer of glove is to be worn (no inner layers). The use of thin gloves that are internally “dusted” with talc, or other powder, is undesirable in respect of risks to the system. Gloves shall be regularly checked for contamination e.g. by oil and grease, and any contaminated gloves are to be replaced. Hand gloves are to be the standard item used, however, where there is a specific requirement identified in the process risk assessment for the operator to have to work with hands at or above chest level gauntlet style gloves may be used.

            1. A face shield prevents injury to exposed skin and particularly the eyes. In addition to the face shield, the use of safety glasses which specifically protect the eyes from liquid ingress should be considered as part of the PPE Assessment.

            1. The wearing of jewellery specifically on the hands and wrists e.g., watches, rings, is not recommended when working with cryogenic liquids.

            1. It is recommended that, wherever practicable, NBC (nuclear, biological, chemical) equipment is NOT worn in a cryogenic liquid’s environment. When there is a requirement to wear NBC equipment, oxygen bay protective clothing is to be worn over the top of the NBC equipment. Pure carbon (in the form of charcoal or activated carbon) is shock sensitive when contaminated with liquid or gaseous oxygen; and, if ignited, burns explosively. Layers of carbon-impregnated cloth may be found within NBC clothing; carbon may also be present in NBC filters

            1. The wearing of NBC equipment in a cryogenic liquid environment is to be specifically addressed when carrying out the documented Risk Assessment.

Table 2.3 - Summary of PPE for use with cryogenic liquids
Body area	Protection required
Hands	PVC or leather gloves should always be worn when handling anything that is, or may have been, in contact with cold liquids or vapours. (BS EN 511). Gloves should be a loose fit so that they may be readily removed should liquid splash onto them or into them, or in case of “freezing” onto cold metal parts. Gloves should incorporate an elasticated knitted wrist. Sleeves should cover the ends of the gloves.
Feet	Safety boots (BS EN ISO 20345). The impact resistant toecaps shall be internal. No steel tips (hobnails) on sole or heel. Anti-static sole. Metatarsal (midsole) protection recommended.
Eyes	Safety eye / face protection (BS EN 166). Chemical goggles or face shield. The face shield prevents injury to exposed skin and particularly the eyes.
Clothing	Non-nylon, Coverall FR or similar type clothing should be worn. Long sleeves / legs so that the skin is not exposed. No open pockets or turn-ups where liquid can collect. Overalls to be secured at the wrist. Cuffs should be double layered to prevent the ingress of liquid. Gloves secured over the inner layer. Trousers to be worn outside boots. Water-resistant outer clothing, manufactured from a material with close-formed fabric, such as Gortex™, is recommended.

            1. Annex A to this Chapter details the recommended PPE / clothing for use in cryogenic environment.

## Bibliography

            1. JSP 375: Management of Health and Safety in Defence

            1. Defence Clothing Catalogue, Section AT2/10, DMC V052, Freezer Wear, High Visibility and Protective Clothing

            1. JSP 515: The MOD Hazardous Stores Information System.

            1. BS EN 166 - Personal Eye Protection. Specifications.

            1. BS EN 169 - Personal Eye Protection. Filters for Welding and Related Techniques.

            1. BS EN 175 - Personal Protection. Equipment for Eye and Face Protection during Welding and Allied Processes.

            1. BS EN ISO 20345 - Personal Protective Equipment. Safety Footwear.

            1. BS EN 374 - Protective Gloves against Chemicals and Micro-Organisms.

            1. BS EN 388 - Protective Gloves against Mechanical Risks.

            1. BS ISO 1611: 2007 - Protective Clothing for Use in Welding and Allied Processes. General Requirements.

            1. BS EN 511 - Protective Gloves against Cold.

            1. BS EN 529 - Respiratory Protective Devices. Recommendations for Selection, Use, Care and Maintenance. Guidance Document.

            1. BS EN ISO 11612 - Protective clothing. Clothing to protect against heat and flame.

            1. BS EN 12477 - Protective Gloves for Welders.

# Annex A - Recommended PPE / Clothing for use in a Cryogenic Environment

Table 2.A.1 - PPE Clothing (NSN List)
Body area	Item, description	NSN
Head	Helmet	8415-99-132-1013 (White) / 8415-99-132-1014 (Blue) / 8415-99-132-1015 (Orange) / 8415-99-869-1902 (Yellow) / 8415-99-920-0977 (Red)
	Frame Attachment Industrial Safety Helmet	4240-99-662-8437
	Headband Industrial Faceshield (when helmet is not worn).	4240-99-978-8777
	Visor Faceshield (for above)	4240-99-978-8781 / 4240-99-978-8784
	Chin guard (for above)	4240-99-978-8787
	Ear defenders (for helmet)	4240-99-132-1371
Hands	Gloves, Cryogenic	Awaiting NSN
Feet	High Leg Safety Boots	8430-99-297-6732 / 6734 / 8430-99-869-1170 / 1184 / 8430-99-2822339 / 2341
Body	Coverall FR Navy Blue	8405-99-869-6250 / 6262
	Coverall FP Green	8415-99-225-7261 / 7273
	Smock (POL Suit)	8415-99-361-7736 (Small) / 8415-99-361-7737 (Medium) / 8415-99-361-7738 (Large) / 8415-99-361-7739 (Extra Large)
	Salopettes (POL Suit)	8415-99-361-7740 (Small) / 8415-99-361-7741 (Medium) / 8415-99-361-7742 (Large) / 8415-99-361-7743 (Extra Large)
Misc	Storage bag	8415-99-5003933

Helmet
Ear Defenders
Visor Mount Assembly
Visor
Smock
(POL) Suit
Salopettes
(POL) Suit
Gloves
Cryogenic
High Leg
Safety Boots
Figure 2.A.1 - Recommended PPE / Clothing for use in a Cryogenic Environment (Pictorial)

# 3 - Identification of Gas Receptacles

Chapter Sponsor - DSFA Technical Gases Manager

## Scope

            1. This chapter provides information on primary and secondary identification labelling and marking used to indicate the contents of a gas cylinder and the associated hazard(s) of the gas.

WARNING: The precautionary label is not to be removed or tampered with in any way.

WARNING: The colour of the cylinder is not to be altered.

WARNING: Pre-stamped markings are not to be altered in any way.

WARNING: Cylinders shall not be marked by stamping data on the cylindrical section.

## General

            1. Gas cylinders are supplied in various shapes and sizes, from small cylinders to banks of manifolded cylinders. The common sizes in general circulation are from 5 to 50 litres water capacity, ranging from 500 mm to 1500 mm in height and 150 mm to 230 mm in diameter. Weights range from 8 kg to 80 kg.

            1. The shape of a cylinder does not provide any reliable information about its contents. LPG cylinders, however, when compared with other compressed gas cylinders, are wider and more squat in shape and are usually fitted with a welded foot ring making the standing cylinder more stable than others.

## Standard Identification Marking

            1. Cylinder identification. The contents of a cylinder are primarily indicated by the information on its precautionary label. A secondary method of identification is by the colour code painted onto the cylinder; or more specifically onto the cylinder shoulder[3].
              [3] Colour coding of cylinder in MCP/bundles/packs is not a requirement under BS EN 1089-3.

            1. Contractor owned receptacles are most likely to be marked in accordance with the following standards:

BS EN ISO 13769:2018 - Gas Cylinders. Stamp marking.

BS EN ISO 7225:2007+A1:2012, Gas cylinders. Precautionary labels.

BS EN 1089-3:2011 Transportable gas cylinders. Gas cylinder identification (excluding LPG). Colour coding.

            1. Medical gases comply with the colour coding system in ISO 32 (ISO 32: 1977, Gas cylinders for medical use - Marking for identification of content).

            1. MOD owned receptacles are marked in accordance with the Defence Standard Def Stan 81 - 24 . Identification Markings of Transportable Receptacles - Compressed Gas.

            1. Deviation from the standard colour and marking codes causes confusion and can be dangerous. The painting and marking of cylinders shall only be carried out by approved contractors or by approved MOD gas cylinder maintenance workshops. Under no circumstances shall stamp-marking, painting, stencilling or local identification markings to be placed on cylinders without the specific permission of the owner (Support Authority) of that cylinder.

            1. Where cylinders are over-packed for transportation, all cylinders within the packaging shall be correctly marked and identified, and the outer packaging is to be accurately marked and identified to show the contents (refer to Part 2, Chap 8).

            1. MOD Identification Marks. The following markings shall be on all MOD cylinders:

  1. The letters ‘MOD’ and the MOD Pheon ‘’ stamp marked on the shoulder.

  1. All MOD owned cylinders shall have a NATO Stock Number (NSN).

  1. The MOD is identified as the owner on the identification label, or

  1. The MOD is identified as the owner from information paint stencilled on the body of the cylinder.

            1. Stamp-marking. Stamp-marking is used to provide durable and legible manufacturing, operational and certification information. Cylinders are stamp-marked by the manufacturers, the owners or by authorised persons only. The name of the industrial gas company will be stamped on the cylinder. This will allow identification as to who the cylinder owner is. For acetylene cylinders, the word “ACETYLENE” is stamped onto the neck. This will allow positive identification as to whether the cylinder is an acetylene cylinder.

            1. On composite cylinders stamp-mark information may be printed on a label that is placed under the resin. This may be on the shoulder or the side-wall of a cylinder.

            1. MOD personnel shall not to stamp-mark any information onto a cylinder without the specific permission of the owner (Support Authority) of that cylinder.

            1. Precautionary labels. The precautionary label is the primary method of identifying a cylinder and its contents (refer to BS EN ISO 7225). Precautionary labels are normally attached to the shoulder area of a cylinder. The purpose of the label is to facilitate the identification of each cylinder and its contents and to warn of the principal hazards associated with those contents, refer to Annex G of this Chapter.

            1. Precautionary labels and diamond hazard labels are allowed to be painted directly onto the cylinder for specified liquefied gases, e.g. LPG. LPG Industry COP 27and ADR refer.

            1. The label shall be maintained on a cylinder such that it remains clearly visible and legible. In the event that a label becomes illegible, or is removed, then the cylinder should be returned, and a serviceable cylinder obtained.

            1. The label will consist of two parts:

A diamond hazard label that identifies the primary and any subsidiary risks associated with the gas contents.

A warning panel with the following information:

  1. Company Name (of the company supplying the gas and receptacles).

  1. Address of the company in the United Kingdom.

  1. Risk and Safety phases relating to the product.

  1. EC label (for pure substances only).

  1. EC number, if applicable.

  1. Product name and the chemical symbol of the gas.

  1. Identification number.

  1. Proper shipping name

            1. The diamond hazard label shall conform to the requirements of the United Nations Recommendations on the Transport of Dangerous Goods, Model regulations. All gases are assigned to Class 2. They are subdivided into one of three divisions based on the primary hazard:

Division 2.1 - Flammable gases.

Division 2.2 - Non-flammable, non-toxic gases.

Division 2.3 - Toxic gases.

            1. A separate label is provided for each of these primary hazards. Where the gas also has a subsidiary risk(s), further diamond hazard labels(s) shall be displayed, such as:

Subsidiary risk 5.1 - Oxidizing substance.

Subsidiary risk 8 - Corrosive substance.

            1. These diamond hazard labels are displayed in Annex E to this Chapter.

            1. Diamond hazard labels may be reduced in size to fit gas cylinders according to the dimensions outlined in BS EN ISO 7225. Labels may overlap, however, the primary risk label and the figures appearing on the label shall remain fully visible and the symbols are recognizable.

            1. Reference is to be made to DGM for the MOD requirement for marking and labelling of dangerous goods during transportation. There are specific requirements for the marking of vehicles carrying dangerous goods. Refer to Part 2, Chapter 8.

## Additional Identification Marking

            1. This way up label. This way up labels shall be displayed on two opposite sides of a package containing liquefied gases. This label is displayed in Annex F to this Chapter.

            1. Cryogenic label. A cryogenic label is required to be displayed on packages containing cryogenic gases. It is compulsory on-air freight. This label is displayed in Annex F to this Chapter.

            1. Tropical fill label. There are two filling ratios to which a gas is supplied within a cylinder in the MOD.

Where the cylinder is to be used within the United Kingdom, then it will be supplied in the ‘full’ condition, at the maximum charge pressure.

If, however, the cylinder is to be supplied to a unit operating in an area where the ambient temperature is likely to be high, there is a danger that the internal pressure will rise, with increasing temperature. To ensure that the cylinder internal pressure stays within the prescribed limits for that cylinder then the cylinder will be supplied with a ‘Tropical Fill’ which will be less than the normal ‘full’ condition. These cylinders shall have a Tropical Fill label attached to them. An example of this label is displayed in Annex G to this Chapter.

            1. Aviation standard gas (STANAG 7146). In order to comply with STANAG 7146-Assignment of NATO code numbers to gases used in aircraft cross-servicing - Certain gases used by NATO armed forces in aircraft cross-servicing operations will be identified with additional information indicating the NATO code number and the NATO product description. These gases are identified in Def Stan 81-24. This information may be included on the precautionary label or, alternatively, an additional label will be attached to the cylinder. The label displayed in Annex G to this Chapter may be used.

            1. Expiry date label. Some gases (e.g. breathing gases and medical gases) are allocated a life. Depending on the gas type this typically ranges from 2 years to 10 years. This is indicated by the supplier using a label attached to the plastic collar, or the upper body, of the cylinder. Once this life has expired the gas is no longer fit-for-purpose and the gas cylinder is to be returned. An example of a typical label is displayed in Annex G to this Chapter.

            1. Identification of contractors cylinders filled by MOD personnel. When it is necessary for MOD personnel to fill contractor-owned cylinders, separate body and shoulder labels shall be attached to contractors cylinders on their 1st fill by MOD personnel stating that the cylinder has been filled by MOD personnel and that it shall have an internal inspection on return to the contractor (refer to Part 2, Chap 5). This label is displayed in Annex G to this Chapter.

            1. These labels are available for demand via the MOD Gas Supply. Contact Team LEIDOS Gases Inventory manager:

Chelsea Hallett
Supply Chain Co-ordinator
OLG and Lab Equipment
TVSSCS / Team Leidos
Work mobile – 07867 254750
Desk Phone – 0117 332 8663
Email - chelsea.hallett102@teamleidos.r.mil.uk
Chelsea.hallett102@teamleidos.mod.uk

Table 3.1 - MOD filled Cylinder Labels
Description	Contractors Part No.	NSN
Label, Contractor cylinder filled by MOD	13165512	71C/0443/7690-99-9287998

            1. It is mandatory for every cylinder to have an initial inspection and test to ensure its serviceability before use, this is followed by regular periodic inspection and tests to ensure its continued serviceability whilst in service. The date that these inspection and tests are carried out is stamp-marked on the cylinder. Following an inspection and test each cylinder is allocated a life before its next periodic inspection and test becomes due. Refer to Annex A to this Chapter.

            1. Cylinder Test Rings. Cylinder test rings provide a quick, visual reference that show when a cylinder is due for its next periodic inspection and test. They normally consist of two brightly coloured plastic discs, fitted between the cylinder and the valve; colour coded and shaped to indicate the month and year when the next periodic inspection and test is due. Refer to Annex A of this Chapter for examples of Cylinder test rings.

            1. A secondary use of these test rings is to indicate when a cylinder has been exposed to excessive heat. If any heat damage is evident on the rings the cylinder shall be returned and replaced with a serviceable item (refer to JSP 319).

            1. Only complete cylinder rings are allowed to be used. If cylinder test rings are damaged, the cylinder shall be returned and replaced with a serviceable item. Only authorised personnel may fit cylinder test rings. Some older cylinders tested to BS EN 1803 could be stamped on the shoulder with the inspection date, yy/mm or yyyy/mm.

            1. Refer to Annex B of this Chapter for examples of cylinder stamp markings.

            1. Plastic collars. Many cylinders rented from contractors will come with a white plastic collar fitted around the neck of the cylinder. This is an approved addition which allows the contractor to display all the technical, legislative and safety information relevant to that particular cylinder and its contents. This white plastic collar shall not be removed. In the event that a white plastic collar becomes removed, the cylinder shall not be used and it is to be returned to the contractor.

            1. Colour coding. Colour coding, based on BS EN 1089-3, is a secondary method of identifying the contents of a gas cylinder. Colour coding is applied solely to the shoulder, or curved part, at the top of the cylinder, and is used to identify the hazard associated with the gas in the cylinder. Certain gases have been allocated a specific colour. Two concentric bands, or quartering, may be used to show where a gas has more than one hazard. While this colour code is being used to provide a degree of conformity, it is not a mandatory standard, and has not been adopted by all gas companies. Each gas company is allowed to adopt its own colours for the main body of the cylinder. Cylinders of common product packs from the MOD gas supply contractor are colour coded. There are two classes of cylinders that are supplied in grey generic colour. They are:

Cylinders in MCPs. The identification of the product will be on the label as name banner labels attached on front and rear of the MCP frames. The name banner labels also include product code for end users to identify by means of a recipe code.

Cylinders for product specific packs, ie specific gas mix requested by the MOD. The identification of the product will be on the label as name banners on the cylinder collars. The name banner labels also include product code for end users to identify by means of a recipe code.

            1. Many 'recovery' cylinders make use of a yellow band, usually around the shoulder, valve guard or upper portion of the cylinder. This will have the word "RECOVERY" or "RECOVERED REFRIGERANT" stencilled onto the band, normally in black in 50 mm letters. This is to highlight the fact that it has been used to recover product from a system and is likely to have some contamination. Recovery cylinders are typically used with refrigerants, or other controlled gases such as SF6 (refer to Part 2, Chap 14).

            1. As a general rule, suppliers of refrigerant cylinders do not follow the colour standard detailed in BS EN 1089-3. It should be noted that the colour schemes applied to refrigerant cylinders differ between the various gas supply companies. Details of the colour scheme used by the current MOD Gases contractor are published on the Team LEIDOS / MOD Contractors Website.

            1. As a general rule, suppliers of LPG cylinders do not follow the colour standard detailed in BS EN 1089-3. It should be noted that the colour schemes applied to LPG cylinders differ between the various gas supply companies. Within the UK (LPG Industry COP 27 refers) the following colour schemes are typical:

  1. Propane with vapour off-take and manual valves – red.

  1. Propane with vapour off-take and self-closing valves – red; or green but with either a red shroud or fitted with a clearly visible red identifying marker.

  1. Propane with liquid off-take and manual valves – red or red with the cylinder shroud black.

  1. Butane – blue.

            1. The system of colour coding is based on a paint chart (RAL 840 HR) developed by Reichs-Ausschus für Lieferbedingungen (RAL) in Germany. It is in-line with European standards, such as BS EN 1089-3; and, whenever practical, it is used on all transportable gas cylinders used by the MOD.

            1. Apart from medical gases, the colour coding system is not mandatory. There is no universal colour coding standard. Different Nations, manufacturers, etc, may apply different colours for the same gas. Colour coding is not to be relied upon as the sole means of identifying the contents of a gas receptacles.

            1. Gases, and gas mixtures, are identified by a colour classification indicating the property of the contents in accordance with the risk diamond on cylinder labels.

Table 3.2 - Gas Cylinder Colour Coding based on Gas properties.
Hazard Label	Colour Code
Toxic and/or corrosive	Yellow
Flammable	Red
Oxidizing	Light Blue
Inert (non-toxic, non-corrosive, non-flammable, non-oxidizing)	Bright Green

Inert gas cylinder – pureshield argon

            1. The colour Bright Green is not used for inhalation (e.g. breathing apparatus).

            1. When a gas or mixture has two hazard properties then the cylinder shoulder is coloured in accordance with the primary hazard.

            1. The colour of the secondary hazard can also be applied to the cylinder shoulder. The colours may be applied either as bands or quadrants.

Table 3.3 - Gas Cylinder Colour Coding with Primary / Secondary Hazards
Hazard Label	Colour Code
Toxic (and/or corrosive) and flammable	Yellow plus Red
Toxic (and/or corrosive) and oxidizing	Yellow plus Light Blue

            1. Specific gases. The following gases are identified by specific colours:

Table 3.4 - Specific Gas hazard Cylinder Colour Coding
Specific Gases		Colour Code
Flammable Gas	Acetylene	Maroon
Oxidizing Gases	Oxygen	White
	Nitrous Oxide	Blue

Acetylene cylinder (left) and industrial oxygen cylinder (right).

            1. There are two Maroon colours in use for acetylene. The majority of cylinders within the UK will be coloured in accordance with BS 381C No. 541, but cylinders in Europe will be coloured to RAL 3009 (Oxide Red) in accordance with BS EN 1089-3.

            1. Additionally, inert gases for medical and industrial applications are further differentiated by use of the following colours:

Table 3.5 - Inert Gas hazard Cylinder Colour Coding
Gas	Colour Code
Argon	Dark Green
Nitrogen	Black
Carbon Dioxide	Grey
Helium	Brown

A bundle of carbon dioxide cylinders.

A bundle of nitrogen cylinders.

            1. When inert gases are mixed, combinations of the optional colours of the specific component gases, listed above, can be used to identify the cylinder contents.

            1. Medical and breathing gas mixtures containing oxygen are identified using the following colours. These colours are not used for industrial gas mixtures.

Table 3.6 - Medical Gas hazard Cylinder Colour Coding.
Gas	Colour Code
Air or Synthetic Air	White & Black
Heliox (Oxygen & Helium mix)	White & Brown
Oxygen / Carbon Dioxide	White & Grey
Oxygen / Nitrous oxide	White & Blue
Nitrox (Nitrogen & Oxygen mix)	White & Black
Trimix (Helium, Nitrogen & Oxygen)	White, Black & Brown

Breathing air cylinders.

            1. Valve protection caps fitted to cylinders are not included in the colour code and are generally left unpainted.

            1. Reflective tape on acetylene cylinders. High visibility photo-reflective tape is being applied to all acetylene cylinders provisioned by UK gas suppliers. Its purpose is to make the cylinders more visible, therefore easier to identify, by fire-fighters involved in a fire. Typically, the tape will be positioned on, or just below, the shoulder, and will be in the form of a band around the circumference of the cylinder. Alternatively, some UK companies may apply the tape to a plastic collar around the shoulder. In all cases the tape will have the word “ACETYLENE” printed on it.

            1. This tape shall not be removed. If the tape is excessively damaged or removed, the cylinder shall be declared unserviceable and returned in accordance with DLF.

            1. Exceptionally, where acetylene cylinders are in-use at forward operating bases, and where the use of high visibility tape is not acceptable (in a military context), then the high visibility tape may be covered with a masking tape. All such masking tapes are to be removed when the cylinder is returned from the forward operating base.

## Bibliography

            1. UN Recommendations on the Transport of Dangerous Goods - Model Regulations - Nature, Purpose and Significance of the Recommendations.

            1. ISO 32: 1977 - Gas Cylinders for Medical Use - Marking for Identification of Content.

            1. BS EN 1089-3:2011 - Transportable gas cylinders. Gas cylinder identification (excluding LPG). Colour coding.

            1. BS EN ISO 7225:2007+A1:2012 - Gas Cylinders. Precautionary Labels.

            1. BS EN ISO 13769:2018 - Gas Cylinders. Stamp marking.

            1. STANAG 7146, ASSIGNMENT OF NATO CODE NUMBERS TO GASES USED IN AIRCRAFT CROSS-SERVICING, AAGSP 10, Edition A, Version 1, Jan 2016.

            1. Def Stan 81-024 Identification Marking of Transportable Containers, Compressed Gas.

            1. DSA03 DLSR Movement and Transport Safety Regulations 0 Dangerous Goods Manual (DGM)

            1. LPG Industry Code of Practice 27 - The Carriage of LPG Cylinders by Road & Hazard Information Labelling Requirements

            1. Agreement concerning the International Carriage of Dangerous Goods by Road (ADR)

            1. BS 381C SET: 1996 (R2002) Specification for colours for identification, coding and special purposes.

# Annex A - Cylinder Test Rings

Table 3.A.1 - Cylinder Test Rings

Note:
The sequence of colour and shape of the annual cylinder test rings is repeated on an 18-year cycle, hence 2031 is a repeat of 2013. The cut-out on the monthly ring may be a half circle on the outer diameter of the ring or a full circle within the ring, dependant on the space available. The cut-out will be repeated at 180° intervals.

# Annex B - Stamp Markings for Compressed Gases

Rear
Front
Key
1 standard	13 minimum guaranteed wall thickness
2 country of manufacture	14 identification of aluminium alloy (if applicable)
3 manufacturer's identification	17 working pressure
4 manufacturing serial number	18 maximum permissible filling weight (if filled by weight)
5 stamp for non-destructive examination (if applicable)	20 tare
6 identification of steel compatibility (if applicable)	22 inspection stamp and date of periodic inspection (YY/MM or YYYY/MM)
7 test pressure	23 space for additional optional markings or for application of labels
8 inspection stamp	25 service life for composite cylinders (YYYY/MM) / This example is for a cylinder with an unlimited life
9 initial test date (YYYY/MM)	26 underwater use of composite cylinders
10 empty weight	27 international mark(s)
11 water capacity	28 country of approval for stamp marking No. 27
12 identification of cylinder thread

# Annex C - Stamp Markings for Acetylene Cylinders

Key
1 standard	14 identification of aluminium alloy (if applicable)
2 country of manufacture	15 identification of porous material
3 manufacturer's identification	16 identification of content
4 manufacturing serial number	17 working pressure
5 stamp for non-destructive examination (if applicable)	19 total weight
7 test pressure (PH60BAR or PH52BAR) / The test pressure is either 60 bar or 52 bar iaw ISO 3807.	20 tare: Tare S, or Tare A/S or Tare F
8 inspection stamp	21 identification of solvent for acetylene cylinders
9 initial test date (YYYY/MM)	22 inspection stamp and date of periodic inspection (YY/MM or YYYY/MM)
10 empty weight	23 space for additional optional markings or for application of labels
11 water capacity	24 inspection stamp certifying correct filling of porous material
12 identification of cylinder thread	27 international mark(s)
13 minimum guaranteed wall thickness	28 country of approval for stamp marking No. 27

# Annex D - Stamp Markings for LPG Cylinders

Key
1 handle	4 cylinder neck boss
2 permanently attached nameplate	5 foot ring
3 stamp marking on cylinder body	6 shroud

The permanent markings of metallic LPG cylinders are in three groups as defined by the UN Model Regulations and displayed at one or more of the positions shown in the figure.
# Annex E - Examples of Diamond Hazard Labels used for Gases

Figure 3.E.1		Class 2.1, Flammable gases / Background red; Symbol flame in black or white; Figure 2 in bottom corner. / MOD: F/PKG/252 Package, (100mm x 100mm or 250mm x 250mm)

Figure 3.E.2		Class 2.2, Non-Flammable, Non-Toxic gases / Background green; Symbol gas cylinder, black or white; Figure 2 in bottom corner. / MOD: F/PKG/214 Package (100mm x 100mm or 250mm x 250mm)

Figure 3.E.3		Class 2.3, Toxic Gases / Background white; Symbol skull and crossbones, black; Figure 2 in bottom corner. / MOD: F/PKG/253 Package (100mm x 100mm or 250mm x 250mm)

Figure 3.E.4		Class 5.1, Oxidizing substances / Background yellow; Symbol flame over circle, black; Figure 5.1 in bottom corner. / MOD: F/PKG/259 Package (100mm x 100mm or 250mm x 250mm)

Figure 3.E.5		Class 8, Corrosive substances / Background upper white, lower black; Symbol liquid spilling from 2 glass vessels and attacking a hand and metal, black; Figure 8 in bottom corner. / MOD: F/PKG/264 Package (100mm x 100mm or 250mm x 250mm)

# Annex F - Examples of Labels used When Transporting Liquefied Gases

Figure 3.F.1	This way up labels. Two black or red arrows on white or suitable contrasting background		or
Figure 3.F.2	Cryogenic liquid label

# Annex G - Examples of Labels used on Gas Receptacles

Figure 3.G.1	Example of a Tropical Fill label.
Figure 3.G.2	Example of labels used to indicate compliance with STANAG 7146.
Figure 3.G.3	Examples of labels indicating the life details of a gas.	Use by: 21 Jun 2015 / Gas Life: 5 Years / Return to: M
Figure 3.G.4	Example of labels used to identify contractors’ cylinders filled by MOD personnel. It includes a shoulder label and a body label.

Figure 3.G.5 - Example of Precautionary Label Fitted to Gas Cylinders / Cylinder size code / Product & cylinder size bar code / UN Number / Diamond Hazard Label / Fill Pressure / pressure in bar / Tickopress label
Figure 3.G.6 - Example of Precautionary Label Fitted to Gas Cylinders / Product Licence Number / Gas Description / Directions for use, Storage and Handling precautions / Safety Information / Nominal Gas Volume in Litres

# 4 - Procurement, Maintenance & Disposal of Gas Cylinders

Chapter Sponsor - DSFA Technical Gases Manager

## Scope

            1. This chapter provides information on the manufacture, procurement, maintenance and disposal of transportable gas cylinders.

## Manufacture and Procurement of Transportable Gas Cylinders

            1. Manufacture / procurement of transportable gas cylinders. The MOD does not manufacture its own gas cylinders. However, it is necessary to ensure that all gas cylinders procured for use by the MOD meet the relevant standards shall be safe for use in the military environment.

            1. The following points shall be complied with when procuring a transportable gas cylinder for use in any military platform or equipment:

Gas cylinders are only to be obtained from reputable manufacturers.

All gas cylinders shall be designed and manufactured to an approved standard. The design and manufacturing standard shall be approved by the UK Competent Authority (the Department for Transport (DfT).

Note: U.S. Department of Transport (DoT) cylinders are not currently recognised by the UK Competent Authority.

Cylinders shall be UN marked or Pi marked or Rho marked; and gas cylinders used in breathing apparatus require a CE mark or UKCA mark[4].
[4] Further information on cylinder design standards & the authority for them to be refilled and transported can be found in BCGA Guidance Note 36 (GN 36): Guidance for the Use, Inspection & Transport of Cylinders with Various Design Codes see BCGA FAQ on BREXIT AND TRANSPORTABLE PRESSURE EQUIPMENT for details on Rho mark and GOV.uk on Guidance Using the UKCA marking for details on UKCA mark

All cylinders shall be initially inspected and tested before they are put into service to ensure that they conform to the approved standard. This is to be carried out by an authorised inspection body, if approved this will be indicated with the appropriate stamp-mark on the cylinder (see BS EN ISO 13769:2018 Gas Cylinders. Stamp marking).

All gas cylinders will have to be transportable. They shall meet the appropriate road, rail, sea and air transport regulations for the carriage of dangerous goods, as well as associated UK legislation (refer to Part 2, Chap 8).

The cylinder and its contents shall be correctly identified, by label and colour code (refer to Part 2, Chap 3).

Cylinder and valve materials should be compatible with gas contents (see BS EN ISO 11114-1:2012+A1:2017 for metallic materials and BS EN ISO 11114-2:2013 for non-metallic materials).”

Ensure the cylinder can provide the pressure, capacity and volume flow-rate required.

Determine the space envelope that is available in which to fit the cylinder and its valve.

The valve shall be UN marked or Pi marked or Rho marked.

Where practical use a valve that is operated by a hand-wheel

BS 341-3:2002. Transportable gas receptacles valves. Valve outlet connections.

All cylinders shall be periodically inspected and tested, at appropriate intervals, to ensure that they remain safe whilst in service. This shall be carried out by an authorised inspection body. On satisfactory completion of the periodic inspection and test the date the test was carried out shall be stamp-marked on the gas cylinder (see BS EN ISO 13769:2018 Gas Cylinders. Stamp marking).

The date of the next periodic inspection and test shall be indicated by the use of cylinder test rings (refer to Part 2, Chap 3).

All appropriate drawings, manufacturing, inspection and testing documentation and certification records shall be examined by the Support Authority to ensure the necessary manufacturing requirements have been carried out. These documents are to be safely stored by the Support Authority, or their responsible agents, for the life of the cylinder.

Avoid Special-To-Type cylinders wherever possible. Always seek advice on whether existing in-service cylinders are suitable. Minimising the variety of cylinders increases availability and compatibility and maximises the efficiency of the logistics chain.

            1. Team LEIDOS is the lead organisation for the provision of transportable gas cylinders. Advice can be sought from Team LEIDOS Lubricants and Gases on any aspect of procuring transportable gas cylinders. Contact Details:

Chelsea Hallett
Supply Chain Co-ordinator OLG and Lab Equipment
Tel: +44 (0) 117 332 8663
Work mob 07867 254750
Email: chelsea.hallett102@teamleidos.mod.uk
Chelsea.Hallett102@teamleidos.r.mil.uk

## Valve Protection Devices

            1. The majority of contractor owned gas cylinders are supplied with tamperproof heat-shrink seals covering, in whole or part, the valve outlet and the valve spindle. Many cylinders will have plastic disposable valve caps fitted. These are to be left in place and only removed immediately before use. They help to prevent contamination and provide a visual indication as to whether the gas cylinder has been used.

            1. Many cylinders are fitted with a protective “3/4” valve guard that protects the valve outlet and the valve spindle from mechanical damage during handling, transportation and storage. These guards shall not be removed by the user; access is available to both the outlet and the valve through cut-outs in the guard.

            1. Certain cylinders (e.g. 300 bar Z type cylinders for breathing oxygen and weapon grade Nitrogen) are provided with a spring-loaded plastic valve cap which provides protection for the valve outlet, and prevents the entry of rainwater and other contaminants. These valve caps shall not be removed by the user.

Spring Loaded Plastic Valve Cap
Figure: 4.1 Spring loaded plastic valve cap

            1. Certain cylinders (mainly older designs) are supplied with a metal valve protection cap that screws onto a threaded portion of the cylinder’s shoulder. The valve protection cap shall be kept on the cylinder during handling, transportation and storage; it shall be removed only when the cylinder is in use and refitted immediately afterwards. The user shall be responsible for the safe storage of valve protection caps when they are removed from a cylinder.

## Repair and Testing of Gas Cylinders

            1. Repair/testing of cylinders. Cylinders shall not be repaired, or modified, in service. If a cylinder is determined to be unserviceable it shall be returned, and a serviceable cylinder obtained

            1. Painting, stencilling, re-labelling of cylinders is only to be carried out by authorised persons as detailed by the owner/Support Authority responsible for the cylinder. If the paint finish, marking or labelling require replacement then the cylinder is to be declared unserviceable, it is to be returned and a serviceable cylinder obtained
            2. The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment (Amendment) Regulations, 2011 and Use of Transportable Pressure Equipment (Amendment) Regulations, 2011, define the responsibilities of a number of conformity assessment bodies, i.e. Appointed Persons, Notified Bodies, Approved Bodies, Approved Persons, and Inspection Bodies. In order to attain one or more of these positions an organisation must first gain UKAS Accreditation and then be appointed by the DfT.

            1. Minor repairs may be carried out where refurbishment work does not affect the integrity of the cylinder, but only in UKAS Accredited, DfT Appointed, cylinder test shops by suitably trained, competent personnel.

            1. The Cryogenics and Gas Section (CGS) at DECA Stafford operate a cylinder test shop. CGS has the ability to inspect and test a range of MOD owned cylinders. For further information contact the CGS Technical manager:

Mr John Tipping
CGS Manager
Tel: 01785785181
Mil: 95551 5181
Email: john.tipping@deca.mod.uk

            1. Transportable gas cylinders shall be maintained to the relevant standards which are either those directly referenced in ADR or those recognised by the DfT (or previously by HSE).

            1. MOD owned cylinders that require maintenance or periodic inspection and testing, shall have the work carried out in an UKAS Accredited, DfT Appointed, test shop. Full details of the work carried out are to be recorded on a suitable form (MOD Form 731) ‘Servicing Equipment Conditioning Label’ as detailed in as detailed in MAM-P (Manual of Airworthiness Maintenance – Processes).”Records of this work are to be kept for the life of the cylinder.

            1. Valves shall only be removed from MOD owned cylinders by specifically trained personnel using procedures that ensure that either the cylinder does not contain any pressure or that the valve is captured during the removal process.

            1. Manifolded Cylinder Packs. (“Bundles”) Manifolded Cylinder Packs (MCP) - also known as bundles - contain several cylinders (typically 15 or 16) manifolded together, providing a single source of gas. The cylinders will be enclosed in a robust framework.

            1. MCPs are designed and supplied as an individual unit:

  1. Do not modify or attempt to disassemble a MCP.

  1. Cylinders are never to be removed.

  1. No direct heat source is to be applied to the frame, cylinders or manifold.

## Disposal of Cylinders

            1. Disposal of cylinders. When a gas cylinder is determined to be unfit for further service, or if it is no longer required for use by the MOD, disposal action shall be taken. Advice/authority shall be sought from the Support Authority responsible for the cylinder. There are generally two courses of action to be taken for MOD owned cylinders. Only the owner of a cylinder can authorise the disposal of a cylinder. In all cases cylinders which are provided to the MOD under a rental agreement shall be returned to the contractor. Any disposal action will remain the contractor’s responsibility.

  1. If serviceable, the cylinder may be placed on the market for re-sale via the Disposal Services Agency.

  1. If unserviceable, or of no market value, the cylinder is rendered unfit for future use as a gas receptacle and is scrapped.

            1. There are specific requirements which have to be followed when scrapping a gas receptacle. CGS at DECA Stafford has the facility to correctly mutilate and dispose of gas receptacles. Alternatively, there is an arrangement with Team LEIDOS who manage the Gases contractor with regards to the disposal of gas cylinders. Advice can be sought from:

Chelsea Hallett
Supply Chain Co-ordinator OLG and Lab Equipment
Tel: +44 (0) 117 332 8663
Work Mob: 07867 254750
Email: chelsea.hallett102@teamleidos.mod.uk
Chelsea.Hallett102@teamleidos.r.mil.uk

# Annex A – Gas Supplier Contact Details

General Enquiries: 0800 111 333 or custserv@boc.com

Emergencies & Incidents: 0800 111 333

Industrial/Healthcare Products: 0800 111 333 / orders@boc.com

For order placement and enquiries relating to industrial gases, industrial products, safety products, healthcare, medical gases or related services offered by BOC.

Speciality Gases: 0800 020 800 / orders@boc.com

For order placement, and enquires relating to high purity gases, mixtures, refrigerants and gas control equipment.

Export email address - gbwor.modexports@boc.com

Projects and Technical Support for MOD/DSTL & Ministry of Justice:
Mr Lee Cookson
Customer Development Executive
Projects & Technical Support for Ministry of Defence, DSTL & Ministry of Justice
Mobil: 07385 361804
Email: Lee.cookson@boc.com

## Bibliography

            1. European Commission for Europe. Inland Transport Committee Restructured - Agreement for the International Carriage of Dangerous goods by Road

            1. The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations, 2009.

            1. The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations, 2011.

            1. BS 341-3:2002. Transportable gas receptacles valves. Valve outlet connections.

            1. BS EN ISO 11114-1:2012+A1:2017. Gas cylinders. Compatibility of cylinder and valve materials with gas contents. Metallic materials.

            1. BS EN ISO 11114-2:2013. Gas cylinders. Compatibility of cylinder and valve materials with gas contents. Non-metallic materials.

            1. BS EN ISO 13769:2018. Gas cylinders. Stamp marking.

            1. MAM-P – Manual of Airworthiness Maintenance – Processes.

# 5 - Gas Production and Cylinder Filling

Sponsor - AC Commodities PT & DECA CGMS Stafford

## Scope

WARNING: This publication does not provide the authority for cylinders to be filled but provides generic information on equipment that is available for use in the MOD that can be used to fill gas cylinders.

            1. This chapter provides information on equipment that is available for use in the MOD that can be used to fill a gas cylinder. It highlights those gas cylinders that shall not be allowed to be filled by MOD personnel and details the generic safety procedures to be followed on an authorised gas cylinder during pre-filling, filling, and post filling. It is the duty of Platform and Equipment Sponsors / Support Authorities who manage / operate bespoke gas cylinders within their systems equipment and platforms, to ensure that specific Standard Operating Procedures (SOPs) for safe filling are included in their equipment / platform publications.

            1. Examples of equipment using gas cylinders not managed by the Contractor /Team LEIDOS Lubricants and Gases (e.g. MOD owned cylinders) not included within this chapter are: (list not exhaustive).

  1. Aircraft LOx/ GOx cylinders.

  1. Aircraft Survival Equipment (SE) cylinders.

  1. Aircraft Ground Support Equipment cylinders (e.g., Juniper rigs, Tyre Inflation Rigs)

## General

WARNING: Anyone producing gas or carrying out the filling of gas cylinders is to wear the appropriate personal protective equipment refer to Part 2, Chap 2.

WARNING: Before using any hazardous substance or material, the user is to be conversant with the hazards and associated information detailed on the applicable Safety Data Sheet.

## Gas Production Equipment

            1. Gas Production Equipment. The majority of gas cylinders are supplied for the MOD, filled with the appropriate gas, through the direct supply contract managed by the Team LEIDOS Lubricants and Gases via its prime contractor.

            1. The production of gases is to be strictly controlled within the military environment. This activity is only to be carried out by appropriately trained, authorised and competent personnel.

Liquid Oxygen and Liquid Nitrogen Production Plant. Aviation standard liquid oxygen, liquid nitrogen, gaseous breathing oxygen and gaseous nitrogen may be produced by the Liquid Oxygen and Liquid Nitrogen Production Plant. The Support Authority for this plant is the AC PT. The equipment is operated and maintained by appropriately qualified and trained personnel.

Table 5.1 - Equipment details
Item description	Publication	NSN
Liquid Oxygen and Liquid Nitrogen Production Plant	DAP 119L-0404-1236A+5F	71AS / 3655-01-323-4670
High Pressure Nitrogen Charging Panel, MK 8	DAP 119L-0612-123+5F	71AS / 3655-99-251-9029
High Pressure Oxygen Charging Panel, MK 8	DAP 119L-0612-123+5F	71AS / 3655-99-568-5943

Only personnel who have been formally trained (on the equipment Support Authority authorised course) in plant operations, and received the appropriate 'Q' annotation, are permitted to operate this equipment. The names of such personnel are to be clearly displayed adjacent to the equipment.

Cylinders are only to be filled via the High Pressure Oxygen & Nitrogen Charging Panels, MK 8, with the prior approval of the Team LEIDOS Lubricants and Gases team and the AC PT; and all cylinders so filled shall be clearly identified with permanently attached labels (see Part 2 Chap 3).

The cylinder filling procedure detailed in the relevant equipment publications is to be followed.

Oxygen and nitrogen produced by these plants is required to comply with Defence Standard 68-284 and Defence Standard 58-96 respectively.

Nitrogen Concentration Trolley. Aviation standard gaseous nitrogen may be produced using the Nitrogen Concentration Trolley (NCT). Only personnel who have been formally trained (on the equipment Support Authority authorised course) in operating the NCT, and received the appropriate Q annotation, are permitted to operate the NCT.

The Support Authority for this plant is the AC PT.

Table 5.2 - Equipment details
Item description	Publication	NSN
Nitrogen Concentration Trolley	DAP 119F-2746-123 & 5F	71N/1730-01-5031613
Cylinder Filling System - Nitrogen	GSE Schedule 03/05 (DAP)	71N/3650-99-5211512

The Cylinder Filling System is used to support cylinders (an ‘A’ frame) during the filling process and utilises a common manifold which allows sampling of the gas to take place. The Cylinder Filling System can be stowed in its transit case when not in use.

The Support Authority for this plant is the AC PT.

When the NCT is to be used to fill cylinders, it is necessary to use the Cylinder Filling System and to monitor the water content using the Cermax Dewpoint Meter. The prior approval of the Team LEIDOS Lubricants and Gases team and the AC PT is to be obtained before filling cylinders; and all cylinders so filled shall be clearly identified with permanently attached labels (see Part 2 Chap 3).

The cylinder filling procedure detailed in the equipment publications is to be followed.

Nitrogen produced by this equipment is required to comply with Def Stan 58-96.

Filling from liquid or gaseous pressure systems. Before filling cylinders or other pressure receptacles from any pressure system, the user is to ensure that the system is designed and authorised for that purpose. Gas, or cryogenic liquid, storage systems and their associated pipe work and protective devices are classed as pressure systems and are required to comply with the Pressure Systems Safety Regulations, 2000; there are certain exceptions, but most if not all such systems in cryogenic liquids and gases workshops will be subject to these regulations. JSP 375, Vol 1, Chapter 29 refers. Reference is also to be made to Defence Estates Safety Rules and Procedures 02, JSP 375, Vol 3. These regulations, amongst others, require that a written scheme of examination is completed for each pressure system.

Air Compressors. All air compressors and their associated pipelines shall conform to the Pressure Systems Safety Regulations (PSSR) 2000. All air compressors shall have regular maintenance, inspection and testing, for which procedures shall be laid down and records kept.

All compressed air pipelines and outlets are to be clearly identified with their contents and working pressure JSP 375 Vol 3. All component parts shall be bonded together and the whole system bonded to earth, with a maximum resistance to earth of 10 ohm.

Air Compressors for filling breathing air / diving quality air cylinders. Breathing air compressor systems shall be designed, built and operated in accordance with a recognised standard. (e.g. BS EN 529, or the (maritime) Defence Standards 02-314, 02-316 and 02-373, as appropriate).

Portable breathing air compressor.

WARNING: Workshop based air compressors shall not be used to provide breathing air for cylinder charging.

Compressors shall only be operated by competent personnel who have received appropriate training and authorisation.

To minimise the risk of introducing contaminants compressors shall be sited in a well-ventilated and clean environment. Inlet air to the compressor shall be drawn from an area that is free from potentially flammable, noxious or corrosive concentrations of fumes or vapours, including vehicle, plant and aircraft exhaust fumes. When in use care is to be taken that inlet, air is not excessively laden with moisture or dust.

Compressors that provide breathing quality air shall be clearly identified as such. All breathing air shall be tested on a regular basis and is to meet the specifications and requirements detailed in Part 2, Chap 6.

## General Requirements for Filling Cylinders

Filling gas cylinders. The filling of pressure receptacles shall only be carried out using authorised/approved appropriate equipment, with qualified, trained, competent staff using the relevant standards and procedures.

Personnel filling cylinders shall not carry out any defect rectification, painting or stencilling on cylinders. If any cylinder requires maintenance shall be returned as unserviceable and a serviceable item obtained. The cylinder shall be returned, with an appropriately annotated Equipment Conditioning Label (e.g. MOD Form 731, AFG 1043). (Refer to DLF).

Medical gas. Service units shall NOT manufacture gases for medical purposes, or fill medical cylinders, without the appropriate authorisation from M&GS Team, AC PT and Team LEIDOS Lubricants and Gases Team (refer to Part 2, Chap 15).

Acetylene. Service units are NOT to manufacture acetylene or fill acetylene cylinders. All acetylene cylinders are to be obtained via the Team LEIDOS Lubes and Gases direct supply contract; or, for overseas deployment from an approved local supplier, subject to prior authorisation from Team LEIDOS Lubricants and Gases team.

Manifolded Cylinder Packs. Manifolded Cylinder Packs of cylinders shall not be filled by MOD personnel without specific authority from the Team LEIDOS Lubricants and Gases team.

Palletized cylinders. All cylinders shall be removed from pallets and independently filled. The only exception is if an authorised written procedure exists which ensures that only serviceable cylinders are filled.

Contamination of gaseous systems. Many gaseous systems, particularly those for aviation or weapons systems are very sensitive to contamination. Experience has shown that it is very easy to contaminate these gaseous systems, especially with water. The user shall ensure that all components, e.g. cylinders, hoses, meters, pipelines, manifolds, etc, are purged and dried before they are connected together. If you have ‘wet’ hoses, components or test equipment, it can take days to dry out, and once contaminated some hoses will never dry. In particular it is very important to ensure that all components are manufactured from suitable materials i.e. materials that are not hydroscopic and that will not react with the gas. It is also beneficial to keep the system as compact as possible, with minimum hose / pipe lengths. When not in use, all open orifices shall be sealed to prevent any possible contamination.

Flexible hoses. Whether flexible hoses are installed as part of a pressure system, or independently provided for filling purposes, they shall be approved and supplied by the system sponsor. They shall be inspected for their suitability for the particular gas to be delivered, their pressure rating, their expiry date and for any damage. Any unserviceable hoses shall be replaced. Before connecting hoses ensure the inlet / outlets are free from any contamination. When not in use all hoses shall be blanked to minimise any contamination.

Positive pressure valves. Contractor owned cylinders are generally fitted with a positive pressure valve. This will only allow the cylinder to be emptied down to a pressure of around 2 bar, thus maintaining a residual pressure which prevents the ingress of contaminants. If any contractor-owned cylinders are found to have no residual pressure, are suspected of contamination, or have an unacceptable odour, they shall be declared as unserviceable and shall not be filled. Return in accordance with DLF.

Disposable Cylinders. Gas cylinders which are labelled as "disposable", "non-returnable", "non-refillable" or similar shall not be refilled or used as decant/recovery cylinders.

Temporary Facilities for re-filling specialist oxygen cylinders on Operations and Exercises. Where it is necessary to provide temporary facilities for the re-filling of specialist MOD owned oxygen cylinders e.g. in support of military parachutists on operations or exercises, and where it may be impractical to fully comply with the requirements detailed within JSP 319 the procedures. The risk of this activity will be held by the Duty Holder (DH) / Head of Establishment. Wherever possible the guidance provided in this publication coupled with industry standards should be adhered to, therefore enabling the risk of the process and activity to be ‘As Low As Reasonably Practicable’ (ALARP).

## Filling Procedures

WARNING: The safety risk of gas cylinders being weakened by internal corrosion often depends on the quality of the gas being filled and, on the care, taken to minimise the ingress of any potential contaminants by the filler.

Pre-fill procedures. The pre-fill procedures shall include the following checks:

  1. Identify the owner of the cylinder.
  2. Ensure the cylinder is correctly marked and identified.
  3. Examine the cylinder for serviceability.
  4. Verification of internal cylinder condition.
  5. Verification of integrity of neck ring/threaded boss.
  6. Verification of valve integrity and suitability.
  7. A check for the correct filling pressure.
  8. Check that the cylinder is in date for its periodic inspection and test.
  9. Verification of the tare weight (liquefied gases).

Identify the owner of the cylinder. Before filling, the identity of the owner of a cylinder shall be established (refer to Part 2, Chap 3) and their authorisation to fill the cylinder obtained. MOD owned cylinders can be filled by suitably trained MOD personnel where this is required and authorised within the appropriate publication. Contractor owned cylinders, rented by the MOD, shall only be filled if authority is granted by Team LEIDOS Lubricants and Gases (or relevant Support Authority) and the contractor. Standing authorisations to fill contractor owned cylinders are listed in Annex A to this Chapter. If it is required to fill a contractor owned cylinder that is not listed, authority shall first to be obtained from Team LEIDOS Lubricants and Gases (or relevant Support Authority).

Ensure the cylinder is correctly marked and identified. The cylinder shall be correctly marked, and the contents accurately identified. The proposed contents shall correspond with the identification label and shoulder colour on the cylinder (refer to Part 2, Chap 3).

MOD personnel shall NOT change the contents of any cylinder from its intended service. If there is any doubt as to the contents of a cylinder, then it shall be returned and replaced with a serviceable item. If there is any falsification or defacing of markings it shall be returned as unserviceable (refer to Part 2, Chap 3 and DLF - returns).

Examine the cylinder for serviceability. Operators shall ensure that the cylinder to be filled is in a serviceable condition and that there is no damage which might affect safety. Generic examples are (but not limited to):

The cylinder shall be clean and free of foreign material (such that the cylinder can be assessed for mechanical damage that would prevent it from being filled safely).

The cylinder shall be clean and free of all oil and grease.

The cylinder shall not to be filled if it displays any abnormalities such as arc burns, bulging, severe corrosion, heat/fire damage or significant mechanical damage.

There are to be no illicit repairs.

It is particularly important that the bases of welded cylinders are inspected for corrosion or rusting. Any evidence of such corrosion shall render the cylinder unserviceable.

Unserviceable cylinders shall be clearly identified as such and are not to be filled. Return in accordance with DLF If required, contact Team LEIDOS Lubricants and Gases for further advice.

Ensure the compatibility of the cylinder for filling with the product to be carried (see BS EN ISO 11114).

Ensure the cylinder and its accessories conform to current standards and regulations.

From the marking on the cylinder, establish that it has been examined by a relevant inspection body (refer to Part 2, Chap 3). Ensure that the cylinder is permitted to be filled in the country of the filling station.

Verification of internal cylinder condition. Where it is possible that liquid can get into cylinders, internal corrosion can occur. Cylinders without special valves which prevent ingress of contamination e.g. non-return / positive pressure valves, or where there is a risk of internal corrosion of the cylinder material, shall be checked for liquid ingress, when there are doubts about the cylinders internal condition.

This check shall be carried out by using a residual pressure check, or check weighing, or moisture analysis or any other method which could confirm the presence of liquid contamination

If liquid is detected, a visual internal inspection has to be performed by a competent person. Any such cylinders detected in service shall be declared unserviceable and replaced with a serviceable item. Unserviceable cylinders shall be returned with a suitably annotated Equipment Conditioning Label (e.g. MOD Form 731, AFG 1043). Return in accordance with DLF.

Verification of integrity of neck ring/threaded boss. Establish that the neck ring / threaded boss and guard (if fitted) are serviceable for the intended purpose, and that the neck ring, if one exists, is not loose. If there is a permanent valve guard or a welded-on shroud, it shall be checked to ensure it is properly attached.

Verification of valve integrity and suitability. Establish that:

  1. The valve is correctly fitted and not leaking.

  1. The valve is easy to operate.

  1. Any safety devices are undamaged.

  1. The outlet threads and body are not damaged and are in good
     working order.

  1. The hand-wheel, or key operated spindle, is operable.

  1. It is suitable for its intended gas.

  1. It is clean and not contaminated e.g. by oil and grease.

  1. The valve attaches correctly to the filling connector.

A check for the correct filling pressure. All cylinders are designated a particular maximum Working Pressure. Cylinders shall NOT to be filled to any pressure greater than Working Pressure. The Working Pressure should be stamp-marked on the shoulder of the cylinder (see BS EN ISO 13769). Indicated by the letters “PW” followed immediately by the figures for the Working Pressure (in bar), e.g. PW230.

Older cylinders may have a different method of identifying the Working Pressure (refer to Defence Standard 81-24 for examples of pre-2003 markings).

If filling cylinders in locations where the ambient temperature is significantly different (higher) than the UK, there is a danger that the internal pressure will rise, with increasing temperature, above the allowable Working Pressure. To ensure that the cylinder internal pressure stays within the prescribed limits for that cylinder, then the filler shall ensure that the gas filling ratio and developed pressure are appropriate for that location (ambient temperature).

Reference should be made to BCGA CP 35, Filling ratios and developed pressures for liquefied and compressed gases.

Check that the cylinder is in date for its periodic inspection and test. The date of the initial inspection and test and any subsequent periodic inspection and testing will be stamp-marked on the shoulder. As a visual reference the month/year of the due date of the next periodic inspection and test is indicated by coloured plastic cylinder test rings fitted between the cylinder and the valve (refer to Part 2, Chap 3). An out-of-date cylinder shall not be filled. Out-of-date cylinders shall be returned with a suitably annotated Equipment Conditioning Label (e.g. MOD Form 731, AFG 1043), and replaced with a serviceable cylinder. Return in accordance with DLF.

Verification of the tare weight (liquefied gases). The amount of liquefied gas charged into a cylinder is determined by weight, or if charged at a pressure lower than the vapour pressure, by pressure shown on a vapour pressure / temperature chart for that specific gas. The weight of gas to be charged into a cylinder is determined from the water capacity and the filling ratio for the specific gas or by the maximum permissible filling weight, if indicated.

Filling checks. During the filling process the filler shall ensure that:

  1. Filling is carried out in a clean, well-ventilated area, away from sources of ignition and contamination.

  1. All filling equipment shall be designed, constructed and suitable for use with that gas. This is particularly important for oxygen, where all materials used shall be oxygen compatible.

  1. Cylinder valves should always be opened and closed slowly. Rapid movement can result in momentarily high pressures known as the hammer effect.

  1. To help prevent excessive temperature rises cylinders shall not be filled too quickly. This gives time for heat transfer to carry heat energy from the cylinders to the surroundings.

  1. That the valve is not blocked, and that the operation is progressing satisfactorily e.g. temperature rise checks of cylinder.

  1. In the event of any leakage, then filling shall be stopped, and the cylinder/connections vented. The leak is to be rectified before proceeding. Leaks shall NOT be rectified whilst the system is pressurised

  1. Residual or excess gases shall be vented to a safe location, preferably outdoors in a safe, well-ventilated area.

Post Fill Checks. The filler shall ensure that:

It is within its safe operating limits.

It is not overfilled or over pressurised. In the event of inadvertent overfilling, any excess gas must be removed in a safe manner and the cylinder checked for further fitness for service.

For liquefied gases, immediately after disconnecting from the filling line, the weight shall be checked by use of a scale capable of determining the gas content of that cylinder within the tolerances shown at Table 5.3 to this Chapter, according to the cylinder water capacity. The weight of the cylinder shall not exceed the total weight allowed for the cylinder and gas combination.

The valve is closed.

A leak test is carried out. If leakage is suspected check for seat leakage at the valve outlet, also check the interface between the valve and the cylinder. For welded cylinders attention shall also be paid to the welds to ensure the cylinder is free from leaks.

If not required for immediate use, fit appropriate blanks and, if applicable, protection caps.

The valve guard, if fitted, is secure and serviceable.

Ensure the contents and hazards are correctly identified on the Precautionary label, and that the Precautionary label is secure (refer to Part 2, Chapter 3).

If the gas has a life allocated, ensure the date of fill, the gas life and the expiry life are clearly indicated.

When contractor owned cylinders have been filled follow the procedure detailed in Para 57 to this Chapter.

Table 5.3 - Maximum Allowable Deviation in Tare Weight and Gas Weight
Cylinder water capacity (V) / (litres)	Maximum allowable deviation in tare weight / (grammes)
0.5 < V ≤ 5.0	± 50
5.0 < V ≤ 20	± 200
V > 20	± 400

Control procedure to be followed when filling contractor owned cylinders. As well as the previously detailed filling procedures, the following control procedure shall be followed when a contractor owned cylinder is filled by MOD personnel, or by sub-contractors working for the MOD.

Separate body and shoulder labels shall be attached to the contractor’s cylinder on the 1st fill by MOD personnel (or their sub-contractors) stating that the cylinder has been filled by MOD personnel and that it requires an internal inspection on return to the contractor. Details of suitable labels are shown in Part 2, Chap 3. These labels are available via the Team LEIDOS Lubricants and Gases gas supply contract. Contact Team LEIDOS Lubricants and Gases team manager for advice.

All cylinders filled by MOD personnel (or their sub-contractors) shall be used within a controlled environment e.g. a detachment or within a specialist unit. The detachment/specialist unit personnel are to locally control all such cylinders by reference to their individual serial numbers.

When a gas cylinder becomes due for its periodic inspection and test, or is no longer required, it shall be returned to the contractor.

All returned cylinders shall be declared unserviceable. Unserviceable cylinders shall be returned with a suitably annotated Equipment Conditioning Label (e.g. MOD Form 731, AFG 1043).

The label is to state "Cylinder filled by MOD personnel. Internal inspection required before further use". Return in accordance with DLF.

When returning cylinders ensure that an annotated Equipment Conditioning Label (e.g. MOD Form 731, AFG 1043.) and the body and shoulder labels detailed above are securely attached to each cylinder.

Leak Detection. Information on equipment available for leak detection is detailed in
Part 2, Chap 7.

## Bibliography

      1. The Carriage of Dangerous Goods & Use of Transportable Pressure Equipment Regulations 2009.

      1. European Commission for Europe. Inland Transport Committee restructured ADR Agreement for the International Carriage of Dangerous goods by Road

      1. Pressure Systems Safety Regulations.

      1. BCGA Code of Practice 35 - Filling ratios and developed pressures for liquefied and compressed gases.

      1. BS EN 529 - Respiratory Protective Devices - Recommendations for Selection, Use, Care and Maintenance - Guidance Document.

      1. BS EN 1439 - LPG Equipment and Accessories - Transportable Refillable Welded and Brazed Steel Cylinders Liquefied Petroleum Gas (LPG) - Procedure for Checking Before, During and After Filling.

      1. BS EN 1919 - Transportable Gas Cylinders - Cylinders for Liquefied Gases (excluding acetylene and LPG) - Inspection at Time of Filling.

      1. BS EN 1920 - Transportable Gas Cylinders - Cylinders for Compressed Gases (excluding acetylene) - Inspection at Time of Filling.

      1. BS EN ISO 11114 - Transportable Gas Cylinders - Compatibility of Cylinder and Valve Materials with Gas Contents.

      1. BS EN 12021 - Respiratory Protective Devices - Compressed Air for Breathing Apparatus.

      1. BS EN 13096 - Transportable Gas Cylinders - Conditions for Filling Gases into Receptacles - Single Component Gases.

      1. BS EN 13099 - Transportable Gas Cylinders - Conditions for Filling Gas Mixtures into Receptacles.

      1. BS EN 13365 - Transportable Gas Cylinder - Cylinder Bundles for Permanent and Liquefied Gases (excluding acetylene) - Inspection at the Time of Filling.

      1. BS EN 13385 - Transportable Gas Cylinders - Battery Vehicles for Permanent and Liquefied Gases (excluding acetylene) - Inspection at the Time of Filling.

      1. BS EN ISO 13769 - Gas Cylinders Stamp marking.

      1. BS 1710 – Specification of identification of pipelines and services.

      1. Defence Standard 02-314 - Compressed Air Systems (Category 2).

      1. Defence Standard 02-316 - Requirements for Compressed Purification Equipment (Category 2).

      1. Defence Standard 02-373 - Code of Practice for Compressed Air Systems Cleanliness (Category 2).

      1. Defence Standard 58-96 - Pure Gases for Weapons Systems and Detector Cooling Applications.

      1. Defence Standard 68-284 - Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications.

      1. Defence Standard 81-24 - Identification Marking of Transportable Receptacles, Compressed Gas.

# Annex A - Contractors Authorisation to Fill Cylinders

Equipment	Equipment Location	Cylinder Owner	Cylinders allowed to be filled
ASU / 71AS/3655-01-3234670	Falklands / Cyprus / Stafford / Detachments	BOC	Oxygen / 71C/O443/6830-99-1644081 / (BOC - 123-Z) / Nitrogen / 71C/O443/6830-99-2484372 / (BOC - 642-Z)
NCT / 1730-01-5031613	Authorised Training / Detachments	BOC	Nitrogen / 71C/O443/6830-99-2484372 / (BOC - 642-Z)
Juniper Replenishment Rigs	Aviation Maintenance Bays	BOC	Nitrogen / 71C/O443/1730-99-5499095 / (BOC - 157978-V) / Air / 71C/O443/1730-99-2887119 / (BOC - 157977-V)
Airfield Arrester Barrier	Various military airfields	BOC	1. Nitrogen. / 71C/O443/6830-99-7609398 / (BOC - 151302-BC)
Diving Gas Cylinders	All diving units	BOC	1. Breathing Air. / 6830-99-9356401 / (BOC – 154037-YD-CF)
Note: Permission to fill cylinders is obtained by Team LEIDOS Lubricants and Gases Team as part of the contractual agreement with its contractor(s).

# 6 - Gas Testing

Chapter Sponsor - DSFA Technical Gases Manager

## Scope

This chapter is concerned with the testing of gases and cryogenic liquids. It discusses the main categories of gases available under the MOD gas supply contract and describes what user testing, if any, is required. Where user testing is required, the necessary test equipment and the test specifications are referenced.

The test requirements given in this chapter are arranged by end-use categories, e.g.:

Aviation gases and cryogenic liquids (Refer to Part 2, Chap 13).

Diving gases and diving gas mixtures (refer to Part 2, Chap 16).

Other cryogenic liquids (refer to Part 2, Chap’s 11 and 12).

Calibration gas mixtures.

Industrial gases, including welding gases.

Liquefied Petroleum Gases (LPG), in cylinders and bulk (refer to Part 2, Chapters 17, 18, 19).

Medical gases (refer to Part 2, Chap 15).

Refrigerants (refer to Part 2, Chap 14).

## General - Testing

DSFA Technical Gas Manager is the technical authority for the MOD on the quality assurance and the testing of gases and cryogenic liquids. Within DSFA the Technical Gas Manager is responsible for all quality assurance activities. The DSFA Gas Technical Manager will advise on all aspects of gas quality and specification.

The nominated test Laboratory is managed by the current MOD Gas supply Contractor. (See Annex D to this Chapter for laboratory details). The nominated Laboratory has been approved by Team LEIDOS Oils, Lubricants and Gases team and DSFA shall hold the current appropriate United Kingdom Accreditation Service (UKAS) certification. Laboratories other than that identified at Annex D are unable to be approved by Team LEIDOS & DSFA; as other Laboratories will not have been audited / assessed by Team LEIDOS / DSFA technical staff. The nominated Laboratory identified at Annex D also takes part in the NATO Aviators Breathing Oxygen (ABO) Correlation Programme. Refer to Para 6 of this Chapter for details.

Operating Authorities who use the services of test Laboratories other than the nominated Laboratory (Annex D) do so at their own risk. Operating Authorities are to carry out suitable Risk Assessments on their contracted Laboratory to ensure that the competencies of personnel and accreditation of the facility meet the equivalent standards
as that of the MOD nominated Laboratory. Team LEIDOS Lubricants Gases / DSFA technical staff can offer guidance to Operating Authorities to assist them in assessing the competencies / accreditation of 3rd party laboratories; but they are unable to authorise 3rd party Laboratories.

The UK MOD participates in the NATO Aviator’s Breathing Oxygen (ABO) Correlation Programme. The ABO Correlation Programme is managed by the US Air Force Petroleum Office, USAF Wright Paterson AFB. It conducts the programme on behalf of the USA Department of Defence, AFIC, and NATO allies. The ABO Correlation Programme compares and publishes the results obtained by a number of testing facilities following the analysis of identical calibrated ABO samples. Participating laboratories are allocated with an identification number to preserve anonymity, and to encourage openness and honesty. Participating laboratories are therefore able to monitor their own performance against that of their peers. The ABO Correlation Programme is not an international accreditation programme and does not assure the competencies of laboratory staff and quality assurance processes of laboratories. The ABO Correlation Programme therefore provides added value to an existing test laboratories’ quality assurance process.

Before carrying out any work:

Users must be aware of the hazards associated with the use of gases (refer to Part 2, Chap 1).

Users must select and use the necessary Personal Protective Equipment (refer to Part 2, Chap 2).

Users must correctly identify the gas and its receptacles; handle and use them appropriately (refer to Part 2, Chap’s 3 and 7).

If applicable, users must be aware of the hazards and safety requirements of cryogenic liquids (refer to Part 2, Chap’s 11 and 12).

Read the relevant Safety Data Sheets (SDS) (refer to Part 2, Chap 1, Annex A).

## Aviation Gases and Cryogenic Liquids - Testing

Aviation Gaseous Breathing Oxygen Specification. Oxygen in gaseous form intended for use on aircraft for breathing purposes is purchased against, and shall comply with, the requirements specified in Def Stan 68-284 for breathing oxygen. These products are supplied in approved cylinders and MCPs by a gas supply company. Each cylinder or MCP shall have a label indicating the gas Use-By date. This is three years from the date of filling. Users are to confirm the gas is within this shelf life.

On single cylinders the Batch Filling Label and Use-By date label is affixed onto the cylinder neck collar; whilst on MCP’s it will be attached somewhere on the MCP frame.

Users shall carry out moisture (water content) testing on a representative selection of breathing oxygen / aviation nitrogen cylinders and all MCP breathing oxygen / aviation nitrogen cylinder packs before they are put into service. An appropriate dewpoint meter and sampling system (see Para 117 of this Chapter) shall be used to carry out this test.

A pallet of cylinders shall be separated to different batches by fill date. If a batch has 7 or more cylinders, a minimum of 2 cylinders shall be selected for moisture test. If a batch has 6 or less cylinders, a minimum of 1 cylinder shall be selected for moisture test.

If required, the user may carry out an odour test (refer to Annex C to this Chapter).

Breathing oxygen cylinders and MCPs that fail to meet the moisture standard, or the odour test, specified in Defence Standard 68-284, for breathing oxygen, shall be declared unserviceable and returned in accordance with DLF.

Personnel handling / testing these cylinders are to take every precaution necessary to minimise the risk of contamination (refer to Part 2, Chap 7).

The DLSR, FGSR Gas Regulator and DSFA Technical Gases Manager are to be informed of all cases of non-compliance.

For the policy regarding contaminated breathing oxygen systems in aircraft, refer to the respective Manual of Airworthiness Maintenance – Processes, MAM-P.” (JSP 319 refers).

Aviation Gaseous Breathing Oxygen, Out of Area Operations (OOA) Operations Specification. Oxygen in gaseous form intended for use on aircraft for breathing purposes produced by the Liquid Oxygen and Liquid Nitrogen Production Plant NSN: 71AS 3655-01-323-4670 by RAF specialist teams is required to comply with the requirements specified in Defence Standard 68-284 for breathing oxygen.

Refer to Para’s 4 to 7 to this Chapter for user testing requirements; and Part 2, Chap 5, for the filling of gas cylinders.

Aviation Gaseous Nitrogen Specification. Nitrogen in gaseous form intended for use on aircraft and missile systems is purchased against, and shall comply with, the requirements specified in Def Stan 58-96, Clause 7. These products are supplied in approved cylinders and MCPs by a gas supply company.

User testing. Refer to Para 10 & 11 of this chapter.

Nitrogen cylinders and MCPs that fail to meet the specification for moisture in Defence Standard 58-96, Clause 7, shall be declared unserviceable and returned in accordance with JSP 319, Part 2, Chapter 4.

Personnel handling / testing these cylinders are to take every precaution necessary to minimise the risk of contamination (refer to Part 2, Chap 7).

DSFA Technical Gas Manager is to be informed of all cases of non-compliance.

Aviation Gaseous Nitrogen, OOA Operations Specification. Nitrogen in gaseous form intended for use on aircraft and missile systems produced by the Liquid Oxygen and Liquid Nitrogen Production Plant - DAP 119L-0404-1236A (NSN: 71AS/3655-01-323-4770) by RAF specialist teams shall comply with Defence Standard 58-96, Clause 9.

Nitrogen in gaseous form intended for use on aircraft and missile systems produced by the Nitrogen Concentration Trolley (NCT) - DAP 119F-2746-123 (NSN 71C/1730-01-503-1613) shall comply with Defence Standard 58-96, Clause 9.

Before this nitrogen is used to fill gas cylinders, its moisture content shall be tested using an appropriate dewpoint meter and sampling system (refer to Para 114 of this Chapter) and compliance with the specification for moisture in Defence Standard 58-96, Clause 9, confirmed.

Note:
Refer to Part 2, Chap 5 for details regarding the filling of gas cylinders.

Aviation Liquid Oxygen (LOx) and Liquid Nitrogen (LiN). General Requirements and Storage Tank Maintenance. It is recommended that units align their storage tank maintenance activities with the sampling / testing of the product. Extensions to maintenance activities and / or sampling / testing will not be automatically granted, and in all cases require the authority of the appropriate Support Authority.

Product minimum quantity. Unless periodic maintenance is due the contents of in-use MOD owned bulk storage, tanks refer to Table 6.3 of this Chapter for list of tanks are to be maintained to at least 25% of the tank capacity. This will help to prevent a build-up of contamination and reduce the need for purging. If a tank capacity falls below 25% then the tank is to be blown down (refer to Table 6.1 of this Chapter).

Definitions. The terms ‘blow-down’, and subsequent actions to be taken are detailed below in Table 6.1.

Table 6.1 - Definitions of the terms ‘blow-down’ and ‘blow-down, warm-up and purge’, and subsequent actions to be taken.
Definition	Actions
Blow-down.	This is the total removal of liquid oxygen or liquid nitrogen from a storage vessel as rapidly as is practical and safe to do so, by raising the tank to normal decanting pressure, and draining through the bottom fill / drain valves. It is then refilled with fresh product after which a sample of the liquid is to be sent to the Nominated Test Laboratory (see Annex D) for analysis, for the application, conformance to relevant specification is sought. The product is to be quarantined until a satisfactory result has been obtained.
Blow-down, warm-up and purge.	This is the total removal of liquid oxygen or liquid nitrogen from a storage vessel as rapidly as is practical and safe to do so. This is followed by a "warm-up" during which the inner vessel is brought (forced or naturally) to ambient temperature (15°C). When the inner vessel has reached ambient temperature, it is purged using dry gaseous oxygen, or dry, oil-free gaseous nitrogen for LOx vessels, and dry, oil-free gaseous nitrogen for LiN vessels. / On refilling with fresh product, a sample of the liquid is to be sent to the Nominated Test Laboratory (see Annex D) for analysis, for the application, conformance to relevant specification is sought. The product is to be quarantined until a satisfactory result has been obtained.

Sampling. Sampling of MOD owned LOx/LiN storage tanks, gas production plants and aircraft replenishment trolleys are a unit engineering responsibility. Cryogenic liquids are sampled using the Cryogenic Sampler (refer to Para 115 of this Chapter). Once a sample has been taken, a RAF Form 3811 and the sample is to be sent to the Nominated Test Laboratory (see Annex D) as soon as is practical.

The requirement for testing contractor owned tanks is detailed in par 56 to this chapter.

Contamination. All aviation cryogenic gases are to be stored in conditions which ensure that the quality of the product remains within specification. If any maintenance activity is carried out which may introduce contamination, or if contamination is suspected, then the contents of the storage tank are to be quarantined and a sample carried out. Once a sample has been taken, a RAF Form 3811 is to be completed in triplicate and distributed (refer to Annex D) and the sample is to be sent to the Nominated Test Laboratory (refer to Annex D) as soon as is practical. The product is not to be used until a satisfactory result is obtained. If the moisture content exceeds the specification or if the odour is unsatisfactory then a blow-down is to be carried out. If any other contamination is confirmed then the tank is to be blown down, warmed up and purged (refer to Table 6.1 to this Chapter). Records of such ‘blow-downs’ or ‘blow-down, warm up and purges’ are to be recorded on the relevant equipment’s MOD Form 700 Series.

A list of the current in-service cryogenic liquid storage trolleys and tanks are detailed below in Tables 6.2 and 6.3 to this Chapter).

Table 6.2 - MOD Owned LOx / LiN Storage Trolleys
Storage Trolley	Mk. No.	Publication No.
100 litre LOx Trolley / NSN:4920-99-224-9809	-	DAP 119F-2745-123
200 litre LOx Trolley / NSN: 4920-99-613-1752	-	DAP 119F-2745-123
200 litre LOx Trolley / NSN: 4920-99-153-1771	MK 2	DAP 119F-2745-123

Table 6.3 - MOD owned LOx / LiN Storage Tanks
Storage Tank	Mk. No.	Publication No.
2400 litre Tank / LOx - NSN: 3655-99-572-6033 / LiN - NSN: 3655-99-862-3135	MK 1	DAP 119L-0507-123F
2400 litre Tank / LOx - NSN: 3655-99-929-1914 / LiN - NSN: 3655-99-305-2109	MK 2	DAP 119L-0508-123
4000 litre Tank / NSN: 3655-99-305-2109	-	AP 119L-0503-16A / Obsolete Support Publication
9000 litre Tank / LOx - NSN: 8120-99-224-9917	-	DAP 119L-0505-1

The Support Authority for this equipment is the AC PT.

The procurement of aviation cryogenic liquids via local arrangements whilst operating out of area is to be in accordance with the procedures detailed DLF.

Aviation Liquid Oxygen Specification. Oxygen in liquid form intended for breathing purposes is purchased against, and shall comply with, the requirements specified in Defence Standard 68-284 for liquid oxygen.

Certification. The supplier shall provide a a Certificate of Conformity to the Defence Standard procurement specification with each delivery of liquid oxygen. Units shall check the certificate to ensure the product has met the specification. Units shall hold these certificates for a minimum period of 18 months from the date of delivery.

Receipt. The unit shall carry out an odour assessment (refer to Annex A) and a visual examination (refer to Annex B) of the liquid oxygen at the time of delivery and prior to transfer into MOD owned storage tanks. If the product being delivered does not have a valid certificate of conformity, or any contamination is evident from the above tests, the whole delivery shall be rejected. DSFA Technical Gas Manager and Team LEIDOS Lubricants and Gases team manager are to be informed. If required by DSFA, a sample shall be taken from the delivery tanker and sent for analysis to the Nominated Test Laboratory (refer to Annex D).

Aviation Liquid Oxygen. MOD owned storage tanks. Samples of product from all MOD owned LOx bulk storage tanks (refer to Table 2.1.6.3) shall be drawn at weekly intervals by an authorised, trained person and assessed for odour (refer to Annex A) and a visual examination (refer to Annex B) shall be carried out. A record of such weekly sampling is to be recorded on the relevant equipment’s MOD Form 700 Series.

As per recommended in para 27, the requirement for 6-monthly blown down, warm-up and purging of storage tank and the requirement for 6-monthly sampling / testing of the product are integrated as one activity to be carry out every 6 months.

Aviation Liquid Nitrogen Specification. Nitrogen in liquid form intended for use on aircraft and missile systems is purchased against, and shall comply with, the requirements specified in Defence Standard 58-96, Clause 7.

Certification. The supplier shall provide a Certificate of Conformity to the Defence Standard with each delivery of liquid nitrogen. Units shall check the certificate to ensure the product has met the specification. Units shall hold these certificates for a minimum period of 18 months from the date of delivery.

Receipt. The unit shall carry out a visual examination (refer to Annex B) of the liquid nitrogen at the time of delivery and prior to transfer into MOD owned storage tanks. If the product being delivered does not have a valid certificate of conformity, or any contamination is evident from the above tests, the whole delivery shall be rejected. The DSFA Technical Gas Manager and Team LEIDOS Lubricants Gases team manager shall be informed. If required by DSFA, a sample shall be taken from the delivery tanker and sent for analysis to the Nominated Test Laboratory (refer to Annex D).

Aviation Liquid Nitrogen MOD owned storage tanks. Samples of product from all MOD owned LiN storage tanks shall be drawn at weekly intervals by an authorised, trained person and a visual examination (refer to Annex B) carried out. If contamination is suspected, an odour assessment may be carried out in accordance with Annex A, taking due account of all Safety Warning’s. A record of such weekly sampling is to be recorded on the relevant equipment’s MOD Form 700 Series.

Samples of LiN shall be taken from all MOD owned bulk storage tanks (refer to Table 6.3) at each base on a six-monthly basis (refer to Para 27 of this Chapter). Once a sample has been taken, a RAF Form 3811 shall be completed in triplicate and distributed accordingly. The sample shall be sent to the Nominated Test Laboratory (refer to Annex D) as soon as is practical. The RAF Form 3811 should specify that the sample be tested against Defence Standard 58-96, Clause 7.

LiN Bulk Storage Tanks: MOD owned LiN bulk storage tanks shall be blown-down, warmed-up and purged every six months (refer to Table 6.1 and Table 6.3).

LiN Replenishment Trolleys: There is no requirement for 6-monthly blow-down; warm-up and purging of LiN Replenishment Trolleys (refer to Table 6.2). Replenishing trolleys (Table 6.2) are routinely blown down at periods laid down in their associated DAP topic 5F.

Aviation Liquid Oxygen and Liquid Nitrogen. Production Plant and associated 2400 litre Transportable Tanks. For details regarding the operation of the Liquid Oxygen and Liquid Nitrogen Production Plant (DAP 119L-0404-1236A; NSN 71AS/3655-01-323-4670) refer to Part 2, Chap 5.

Samples of gaseous oxygen and/or gaseous nitrogen from the Production Plant shall be taken during every production run and tested by authorised, trained personnel for purity, in accordance with DAP 119L-0404-1236A, for moisture (water content) and trace contaminants using the MIDAC I Series Industrial FTIR Spectrometer (NSN: 71AS/6650-99-134-8762) (refer to DAP 119L-0322-12). The results of these tests shall be recorded and are to be logged in the appropriate manner.

Additional cryogenic liquid samples shall be taken every 3 months from all 2400 litre Liquid Oxygen Transportable Tanks (refer to Table 6.3) which are filled from the Liquid Oxygen and Liquid Nitrogen Production Plant (DAP 119L-0404-1236A; NSN 71AS/3655-01-323-4670). The Cryogenic Sampler (refer to Para 119 to this Chapter) together with the appropriate hose and connector shall be used to take a sample of liquefied gas directly from the appropriate Liquefied Gas Outlet Port from the tank only.

Once a sample has been taken, a RAF Form 3811 shall be completed in triplicate and distributed accordingly. The sample shall be sent to the Nominated Test Laboratory (refer to Annex D) as soon as is practical. The MOD Form 3811 shall specify that the sample be tested against Def Stan 68-284, for liquid oxygen.

Aviation Liquid Oxygen. Replenishment trolleys (100 & 200 litre). For details regarding the MOD owned LOx replenishment trolleys refer to Table 6.2. Units shall carry out an odour assessment (refer to Annex A) and a visual examination (refer to Annex B) of the LOx in aircraft LOx replenishment trolleys before the first use of the trolleys for servicing an aircraft in any 24 hour period.

No laboratory testing of the product within these trolleys is necessary when they are in regular use and replenished from an on-site bulk tank that is subjected to sampling and laboratory testing (approved Team LEIDOS Lubricants Gases contractor supplied storage tanks or MOD tanks detailed in Table 6.3). Aircraft LOx replenishment trolleys shall be blown-down (refer to Table 6.1) when any contamination is suspected. Details of such blow-downs shall be recorded on relevant equipment’s MOD Form 700 Series. LOx trolleys shall be blown-down (refer to Table 6.1) when maintenance operations, which are to be carried out in accordance with the relevant Air Publication (AP), require the opening of the system and the exposure of the contents to the air.

When brought into use after a period of storage, trolleys shall be subject to blow down, warm-up and purge (refer to Table 6.1); and then filled and sampled. A satisfactory laboratory result is to be obtained before the trolley is returned to service.

Where a trolley is used as a stand-alone supply, i.e. not replenished from a Team LEIDOS Lubricants Gases approved bulk tank or MOD tank detailed in Table 6.3 that is subjected to sampling and laboratory testing, a Certificate of Conformity shall be obtained from the LOx supplier and kept by the unit for a minimum period of 18 months. A copy shall be sent to DSFA Technical Gas Manager and Team LEIDOS Lubricants Gases team manager. A sample of the liquid shall be taken from the trolley and the procedure detailed in Para 51 should be followed.

Aviation Liquid Oxygen and Liquid Nitrogen. Contractor owned storage tanks. The contractor will remain responsible for maintaining the quality of any product within their own vessels. The contractor is to supply the user unit with a Certificate of Conformity detailing the quality of the product against the required specification. For aviation standard gases the contractor will sample on a monthly basis and provide a Certificate of Conformity after each sample. Units are to check the certificate to ensure the product has met the specification.

One copy of the Certificate of Conformity shall be retained by the unit and one copy sent to DSFA Technical Gas Manager and Team LEIDOS Lubricants Gases team manager. The unit shall hold these certificates for a minimum period of 18 months from the date of the sample.

Samples of product from aviation gas storage tanks shall be drawn at weekly intervals by a MOD authorised, trained person and a visual examination (refer to Annex B) shall be carried out; and, for liquid oxygen only, assessed for odour (refer to Annex A). For liquid nitrogen, if contamination is suspected, an odour assessment may be carried out in accordance with Annex A, taking due account of all Safety Warnings. A record of such weekly sampling is to be recorded.

The MOD will always retain the right to independently test any product with which it is supplied. If the quality of the product is suspect then a sample shall be taken, a RAF Form 3811 shall be completed in triplicate and distributed (refer to Annex D) and the sample shall be sent to the Nominated Test Laboratory (refer to Annex D) as soon as is practical. RAF Form 3811 shall specify that the sample be tested against the appropriate Defence Standard. Before taking a sample, advice is to be sought from the DSFA Technical Gases Manager.

Compressed Natural Breathing Air (CNBA) for Diving Gases and Gas Mixtures – Testing

Scope. This section provides policy and guidance on Compressed Natural Breathing Air (CNBA), its application, its supply route, its specification, and it’s testing requirements. The specific applications and requirements are detailed in the respective annexes.

Application. CNBA is used in the following areas within MOD:

Diving both military & Adventurous Training – refer to Annex E and Part 2, Chap 16.

Marine life support, marine firefighting, emergency escape on board ships and submarines – refer to Annex F.

Aviation, emergency Breathing Apparatus (BA) – refer to Annex G.

DFRMO firefighting – refer to Annex H.

Workplace uses BA (e.g. confined space, paint spraying) refer to Annex I.

Medical applications refer to Part 2, Chapter 15.

Supply of CNBA. CNBA is supplied either by:

The current gas contractor in approved cylinders or MCPs.

Produced using in-service compressors for:

    1. Supply to MOD cylinders.

    1. To be used directly as part of in-line fed BA.

Specification. Dependant on the customer requirement and / or the respective Project Team specification requirements supported by justification; CNBA for both contractor supplied cylinders / MCPs; and in service compressors (for cylinder fill or in-line supply) shall be supplied/ produced to the latest editions of either:

  1. Def Stan 68-284- Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications.

  1. BS EN 12021 - Respiratory equipment. Compressed gases for breathing apparatus.

General Testing Requirements CNBA supplied in cylinders by Contractor. When provided via the MOD gas supply contract each cylinder will be supplied with a Certificate of Conformity (C of C). Each cylinder or MCP will have a label indicating the gas Use-By Date. Users shall confirm the gas is within this shelf life before use. Additional in-service testing maybe required dependant on MOD Operator use. The C of C is applicable for the gas stored within the contractor’s cylinder only.

CNBA supplied in cylinders by in-service Compressor. Compressor systems employed to produce CNBA fall within the scope of the Pressure Systems Safety Regulations SI 2000 No 128 (PSSR) (Refer to JSP 375, the Control of Substances Hazardous to Health Regulations (COSHH); and guidance given in the latest editions of BS EN 529: Respiratory protective devices - Recommendations for selection, use, care and maintenance. Guidance document). The regulations require an assessment of risks; a scheme of system examinations; and record keeping. This includes a periodical check on the quality and the flow rate of the delivered air.

Testing Regime. The frequency and range of quality testing shall be determined by risk assessment considering the siting of the compressor, any other local factors which might compromise air purity and the capability of test methods to identify any potential contaminants identified as a particular risk. As a minimum, the following requirements are to be met:

Air quality shall be tested locally by a competent person (using appropriate test and sampling equipment) or by a laboratory (in accordance with Para 67 to this Chapter) at least every three months.

Air quality shall be tested by a laboratory (in accordance with Para 68 to this Chapter) at least annually.

Any more stringent test intervals specified in the relevant Annex E-I shall be observed.

Air quality shall be tested immediately by a competent person (using appropriate test and sampling equipment) or by laboratory (in accordance with Para 67) where intrusive maintenance which may have introduced contamination into the system has been completed.

The test methods and purity standards to be applied are defined in the relevant Annex E-I.

Where local air testing by a competent person is required, it shall be conducted using the test equipment detailed in this Chapter at Para 112 - 125.

Where laboratory testing is required, it shall be conducted by a laboratory accredited to the latest edition of BS EN ISO/IEC 17025 with testing of compressed natural breathing air to the specified standard. Using the company specification / technique as documented within the laboratory schedule of accreditation (e.g. Def Stan 68-284, BS EN 12021. Accreditation of the subject laboratory shall be carried out by a Conformity Assessment Body (CAB) operating in accordance with BS EN ISO/IEC 17011. The preferred CAB is UKAS.

The competent person shall carry out an assessment of all test results to ensure that the CNBA remains fit for purpose and within specification. The competent person shall compare the test results achieved on each test against the historical records and shall determine whether any adverse trends are developing and shall take any necessary rectification action. At the annual test, to allow a valid comparison to be made, the laboratory and user test samples shall be taken at the same time and any differences are to be within the chemical detector tube / field sampling device manufacturers stated tolerances.

Portable Compressors/Temporary Sites. As well as complying with the paragraphs above, the assessor shall ensure that wherever a compressor is located, the quality of CNBA it supplies shall not be compromised by nearby contaminants; this is of particular concern where the CNBA supply is from mobile compressors. The quality of CNBA produced by mobile compressors shall be tested each time a compressor is relocated to a new site (dive site).

Record Keeping. Records of all testing carried out shall be kept for a minimum period of six years. All records relating to sampling/testing of gases shall be made available for inspection to authorised external inspection bodies as appropriate. Copies of the latest analysis certification (unit results and independent) shall be posted at the testing points on the system.

## Other Cryogenic Liquids - Testing

Product scope. This category includes cryogenic gases (ie, liquid oxygen, liquid nitrogen, solid carbon dioxide and liquid argon) for engineering maintenance purposes, for medical purposes, or for veterinary requirements.

Liquid oxygen. Used only for engineering maintenance purposes is purchased against, and shall comply with, the requirements specified in BS 4364:1993 (Specification for industrial oxygen).

There is no requirement for User testing/sampling of this product.

Liquid oxygen is also available as a medical gas (refer to Part 2, Chap 15).

Liquid Nitrogen. Used only for engineering maintenance purposes, such as cooling-down bearings and other components for shrink fitting; or for medical or veterinary use is purchased against, and shall comply with, the requirements specified in BS 4366:1993. (Specification for industrial nitrogen).

There is no requirement for User testing/sampling of this product.

Solid Carbon Dioxide. Known also as “Dry Ice” used for engineering purposes, such as cooling-down bearings and other components for shrink-fitting, is purchased against, and shall comply with, the requirements specified in BS 4105:1990. (Specification for liquid carbon dioxide, industrial).

There is no requirement for user testing/sampling of this product.

Liquid carbon dioxide is also available from gas cylinders (refer to Para 101 to this Chapter)

Liquid Argon. The product is sold by purity, such as N5.0 (99.999 % pure). In practice, liquid argon will be stored in insulated tanks and converted to gas for inerting, missile use, or flushing purposes. Where this product is being used to supply gaseous argon for missile or weapons applications, the gas produced shall comply with Def Stan 58-96, Clause 8.

There is no requirement for User testing/sampling of this product. Argon intended for welding purposes is purchased against, and shall comply with, the requirements specified in BS EN ISO 14175:2008. (Welding consumables. Gases and gas mixtures for fusion welding and allied processes).

Calibration Gas Mixtures - Testing

Calibration mixtures for submarine use. Every cylinder of volumetric calibration gas and gas mixture is supplied with a Certificate of Analysis detailing the actual concentrations of the gas mixture. Unless otherwise specified on the Certificate, these calibration gases and gas mixtures shall be regarded as having a “life” of two years from the date of filling the cylinder. If not used up by then, the cylinder shall be replaced with a new calibration gas or mixture at the end of the life period.

Calibration gases for general use. This category includes some pure gases as well as calibration gas mixtures; the latter are made either volumetrically or gravimetrically. Both pure gases and calibration gas mixtures are supplied with a Certificate of Analysis.

Gases and gas mixtures for diving. Some diving gases and gas mixtures are also available in the form of calibration gases to enable test equipment to be calibrated. These calibration gases and gas mixtures shall be regarded as having a "life" of between six months to five years from the date of filling the cylinder dependant on the type of gas or gas mixture involved. The expiry life of the gas will be indicated on a label attached to the cylinder. If not used up by then, the cylinder shall be replaced with a new calibration gas or mixture at the end of the life period

Depending upon its “grade”, every cylinder of Volumetric calibration gas mixture is filled to within ±10% (relative) or ±5% (relative) of its nominal specified mixing ratio; and is then tested by the cylinder filler, who issues a Certificate of Analysis detailing the actual concentrations of the gas mixture. Gravimetric calibration gases are filled to whichever is the greater of ±1% (relative) and ±2ppm; and the mixture is then tested by the cylinder filler, who issues a Certificate of Analysis detailing the actual concentrations of the gas mixture.

The analytical tolerance is divided into three classes: an Alpha standard will be analysed to ±1 % (relative); a Beta standard to ±2 % (relative); and a Certified mixture standard between ±2 and 5% (relative). Thus, a nominal 20% Alpha mixture will be supplied with, e.g., an analytical Certificate of Analysis specifying the contents as: 20.4% (±1%) (Relative) = 20.4 ± 0.2% of the minor component in a balance of the major component. The value indicated is the measured value and the variable is the analytical tolerance. A comparable uncertified mixture would be labelled as e.g. 20% ±10% (relative) (= 20 ± 2%), or ±5% (relative) (= 20 ± 1%), of the minor component in a balance of the major component, depending on the filling grade requested. The value indicated is the nominal value and the variable is the filling tolerance.

No user testing of these calibration gases is necessary.

## Medical Gases- Testing

Medical gases. These gases are procured from the MOD gas supply contractor who holds the necessary medical Product Licences to produce these medical gases. They are manufactured against UK and European Pharmacopoeia Specifications; refer to Part 2, Chap 15 for further details on medical gases.

Medical gas cylinders are typically supplied with a usable life of up to three years. The expiry date of the life will be indicated by a label on the cylinder shoulder area. For examples refer to Part 2, Chap 3, Annex D.

No user testing of medical gases is necessary.

Medical Gas Pipeline Systems. Where Medical Gas Pipeline Systems (MGPS) and Dental Compressed Air and Vacuum System (DAVS) are installed quality testing is to be carried out in compliance with Health Technical Memorandum (HTM 02-01). This requires that an authorised Quality Controller Pharmacist who has specialist knowledge, training and experience of MGPS and DAVS carries out quality testing of the gases whenever contamination is suspected; if the pipeline has been opened to atmosphere; and on a three-monthly routine basis. The Quality Controller Pharmacist will provide a Certificate of Conformity for each gas. For further information refer to Part 2, Chap 15. If the pipeline system is installed on a vehicle / ship platform, the installation and usage should be in line with transport regulations.

## Industrial Gases

Various Industrial Gases not specified elsewhere in this Chapter. To some extent the term “Industrial gases” is a ‘catch all’ category for gases that do not fall into the other named end-use categories. Examples of such gases available under the MOD GAS supply contract are balloon gas, compressed air, sulphur hexafluoride (SF6), liquid nitrogen and liquid carbon dioxide. Of these, balloon gas has no specification, it is helium containing trace amounts of air; the others are covered by British Standard specifications.

No user testing of these gases is required.

Compressed air Compressed air is either supplied, by a gas supply company, in cylinders / MCPs, or by in service MOD compressors.

Where this product is to be used for breathing purposes, refer to the guidance given at Paras 60 - 71 to this Chapter.

Where this product will not be used for breathing, there is no requirement for user testing of contractor filled cylinders / MCPs.

Pure Air. Pure air, to Def Stan 58-96, Clause 8, is a non-breathing gas used for thermal imaging systems, detector cooling and weapon systems. Pure air is available in small special-to-type cylinders; these pure air cylinders are only available from specialist electronics / weapons systems suppliers.

Pure Air Generators, such as the High-Pressure Pure Air Generator, (HIPPAG), provide a means of generating pure air for missiles and replenishing pure air cylinders.

Analysis of cylinders of pure air can be undertaken by the nominated Test Laboratory (refer to Annex D) by prior arrangement through the Team LEIDOS Lubricants Gases team manager.

Carbon dioxide, liquid and gaseous. Carbon dioxide is supplied in gas cylinders which, depending upon their internal valve configuration, will deliver either gaseous carbon dioxide (gas-delivery) or liquid carbon dioxide (liquid-delivery). Cylinders intended to supply liquid carbon dioxide are fitted with an internal dip tube, and this is indicated by a white line painted upon the body of the cylinder; carbon dioxide cylinders without dip tubes do not have a white line.

Liquid-delivery cylinders intended to supply liquid carbon dioxide when the cylinder is vertical are fitted with a long dip tube and this is indicated by a long white line. Other liquid-delivery cylinders only supply liquid carbon dioxide when they are either horizontal or partially inverted: these cylinders are indicated by a short white line, or a curved white line, respectively.

Carbon dioxide is sold by purity, such as Industrial grade (to BS 4105:1990 Specification for liquid carbon dioxide, industrial), N4.5 (99.995% pure), or N5.0 (Research Grade) (99.999% pure). BS 4105, Type 1, Industrial grade liquid carbon dioxide is intended for non-food applications, such as purging, inerting and life-raft inflation; whereas, Type 2 is suitable for industrial food applications, such as beverages, gas packing, food freezing and chilling. Carbon dioxide is also available as a welding gas.

No user testing of this gas is necessary; however, the user shall confirm by external visual inspection that the correct type of cylinder is being used, i.e. gas-delivery or liquid-delivery.

## Liquefied Petroleum Gases

Liquefied Petroleum Gases (LPG), in cylinders and in bulk. These gases are purchased against the requirements specified in the relevant British Standards, such as BS 4250:2014 (Specification for commercial butane and commercial propane). For LPG cylinders and Bulk refer to Part 2, Chap 17,18,19.

No user testing of these gases is necessary.

## Refrigerants

Refrigerants. Refer to Part 2, Chap 14 for further details on Refrigerant gases.

No user testing of these gases is necessary.

## Welding & Cutting Gases

Welding, shielding and cutting gases. These gases include oxygen, acetylene, argon, carbon dioxide, helium, hydrogen, nitrogen and various shielding gases and gas mixtures.

Certificates of Conformity may be requested from the supplier. This should be specified at the time of the demand.

No user testing of the welding, shielding and cutting gases is necessary.

## Test and Sampling Equipment

The following test, measurement and sampling equipment and sampling cylinders are available for use.

The DE&S LE OIP Workshop Portsmouth team has the specific responsibilities for delivering General Purpose Test and Measurement Equipment and Military Equipment Tool Solutions for use within the MOD. They can supply, calibrate and provide advice on test and measurement equipment.

Cermax Dewpoint Meter and Sampling System. This is a portable instrument designed for the measurement of dewpoint and moisture content in gases.The Support Authority for this instrument is DE&S AC PT.

Table 6.4 - Cermax Dewpoint Meter & Sampling System
Item Description	Publication	NSN
Cermax Dewpoint Meter and Sampling System (Air/Nitrogen)	DAP 119L-0321-123	71B/1660-99-7837029
Cermax Dewpoint Meter and Sampling System (Oxygen)	DAP 119L-0321-123	71B/1660-99-9888087

Cosmodyne Cryogenic Sampler. This equipment is charged with a cryogenic liquid which is allowed to vaporise and therefore contain a representative sample of the cryogenic liquid for laboratory analysis. The Support Authority for this equipment is DE&S AC PT.

Table 6.5 - Cosmodyne Cryogenic Sampler
Item Description	Water Capacity	Publication	NSN
Cosmodyne Cryogenic Sampler	4.4 litre	DAP 119L-0323-12	71BG / 6695-00-726-2721

Factair Safe Air Tester. This equipment is designed to allow user testing for the quality of compressed natural breathing air. It consists of a breathing air testing device, which uses disposal chemical reagent tubes for measuring specific contaminants, e.g. carbon dioxide, carbon monoxide and oil mist.

Chemical reagent detector tubes are sometimes “known” by the name of their manufacturer, e.g. “Draeger tubes”, although detector tubes are also made by other manufacturers. These tubes, identified by manufacturer’s part number, are designed to measure a specific gas contaminant, in air, over a specific gas concentration range (refer to specific manufacturer’s handbook for further details).

Detector tubes should be selected in accordance with the test equipment operating instructions. Refer to Table 6.6.

Information on the range of Factair Safe Air Tester equipment and accessories is available in Table 6.6.

Table 6.6 - Factair Safe Air Tester and Accessories
Item description	Support Authority	NSN	Remarks
Factair F3000 Safe Air Tester	DE&S LE OI-Wksp-PMTH	1680-99-598-6300	Factair F3000
Factair F2235 Safe Air Tester	DE&S LE OI-Wksp-PMTH	6630-99-551-8991
Factair F2247 Bench Mounted calibration Set	DE&S LE OI-Wksp-PMTH	4240-99-471-6351
Factair F2247Portable calibration Set	DE&S LE OI-Wksp-PMTH	4240-99-921-5269
Factair F4000 Safe Air Tester	DE&S LE OI-Wksp-PMTH	6665-99-613-3897	Factair F4000 / Manual
Detector tubes: Oil	DE&S LE OI-Wksp-PMTH	6630-12-189-3124	Pt No 6728371
Detector tubes: H2O	DE&S LE OI-Wksp-PMTH	6630-12-189-3127	Pt no 6728531
Detector tubes: CO	DE&S LE OI-Wksp-PMTH	6630-12-189-3125	Pt No 6728511
Detector tubes: CO2	DE&S LE OI-Wksp-PMTH	6630-12-189-3126	Pt No 6728521

RAF Cosford run a training course for the Factair Safe Air Tester, in addition Factair offer a free Online course for the Factair Safe Air Tester.

Diving Gases Sample Cylinder. Diving Gases Sample Cylinder. Sample cylinder for diving gases are supplied via the Team LEIDOS Lubricants and Gases gas supply contract.

Table 6.7 - Diving Gases Sample Cylinder
Item Description	Water Capacity	NSN	Remarks
Diving Gas Sample Cylinder	1.2 litre	6830-99-172-2256	Pt No 165578-AZ

Compressed Breathing Air Sampling Kit. This sampling kit is designed to be used to take samples of compressed breathing air for laboratory analysis. Typically used in conjunction with the Factair Safe Air Tester, refer to Para 119 and Table 6.6.

Table 6.8 - Compressed Breathing Air Sampling Kit
Item Description	Support Authority	NSN
Compressed Breathing Air Sampling Kit	DE&S LE OI-Wksp-PMTH	34E / 6830-99-666-1085

Dominick Hunter Portable Purity Test Kit (BR 6590(013). This equipment is designed to allow user testing for the quality of compressed natural breathing air. The test kit is supplied for use on board HM Ships and Submarines.

Table 6.9 - Compressed Breathing Air Sampling Kit & Sampler Tubes
Item Description	Support Authority	NSN
Dominick Hunter Portable Purity Test Kit	DES Ships MPS MES MAS	6630-99-372-8629 / Pt No 605001310
Detector tubes Oil		6630-99-746-7235 / Pt No 601271379
Detector tubes H2O		6665-99-605-7639 / Pt No 608200462
Detector tubes CO		6630-99-551-0905 / Pt No 601271378
Detector tubes CO2		6665-99-346-4078 / Pt No 608200464

Factair Oil Impactor. An alternative to the Oil Detector Tube detailed in Table 6.6, is the Factair Oil Impactor. Refer to Table 6.10:

Table 6.10 - Factair Oil Impactor
Item Description	Support Authority	NSN
Oil Impactor 0.1 – 1.0 mg/m3	DE&S LE OI-Wksp-PMTH	6630-12-381-7870 / Pt No 8103530

Portable Gas Detector. Portable gas detectors are designed to be clipped to clothing and used as personnel indicators of the local atmosphere. Refer to Table 6.11.

Table 6.11 - Portable Gas Detector
Item Description	Support Authority	NSN
Crowcon Tetra 3 ,4 sensor gas detector / Typical Sensors: Flammable 0-100 % LEL Oxygen 0-25% Hydrogen Sulphide 0-100 ppm Carbon Monoxide 0-500 ppm	DE&S LE OI-Wksp-PMTH	6665-99-667-5938
Crowcon Gasmaster 4 H2S Monitoring System / CROWCON GASMASTER 4	DE&S Ships Maintenance Management	6110-99-152-7882
Altair 5X/IR Multi Gas Detector / ALTAIR 5X	DE&S Ships Maintenance Management	6665-99-337-6436
Altair 4X multigas detector / ALTAIR 4X	DE&S Ships Maintenance Management	6665-99-959-0986

## Bibliography

ISO Standards

BS EN ISO/IEC 17011: Conformity assessment. General requirements for accreditation bodies accrediting conformity assessment bodies.

BS EN ISO/IEC 17025: General requirements for the competence of testing and calibration laboratories.

BS EN ISO 14175:2008 - Welding Consumables – Shielding Gases for Arc Welding and Cutting.

British Standards

BS EN 12021:2014. Respiratory equipment. Compressed gases for breathing apparatus.

BS EN 529:2005. Respiratory protective devices. Recommendations for selection, use, care and maintenance. Guidance document.

BS EN IEC 60376. Specification of technical grade sulphur hexafluoride (SF6) and complementary gases to be used in its mixtures for use in electrical equipment.

BS 4105:1990. Specification for liquid carbon dioxide, industrial.

BS 4250:2014. Specification for commercial butane and commercial propane.

BS 4364:1993. Specification for industrial oxygen.

BS 4366:1993. Specification for industrial nitrogen.

BS 8478:2011. Respiratory protective devices. Breathing gases for diving and hyperbaric applications. Requirements and test methods. Partially replaced by BS EN 12021:2014.

            1. Def Stan 58-096 - Pure gases for weapons systems and detector cooling applications.

            1. Def Stan 68-284 - Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications"

Air Publications

            1. DAP 119L-0001- Gas (Including Liquid Gas) Production, Storage & Test Equipment.

            1. DAP 119L-0320-12 - Breathing Oxygen Odour Test Equipment (71BG/004-1594 & 71BG/562-5580).
            2. DAP 119L 0321 123: - Michell Cermax Dewpoint Meter and Sampling System (Oxygen	71B/1660-99-988-8087) and (Nitrogen 71B/1660-99-7837029).

            1. DAP 119L-0322-12: - MIDAC I Series Industrial FTIR Spectrometer (71AS/6685-99-474-7200).

            1. DAP 119L-0323-12: - Cosmodyne Cryogenic Sampler Type TTU-131/E GEMS Type Code WCA (71BG/6695-99-7262721).

            1. DAP 119L-0404-1236A – Liquid Oxygen and Liquid Nitrogen Production Plant (Sect/Ref 71AS 3234770) 1.5 Ton per day GSE Type Code -XFY

            1. DAP 119L-0612-123: - High Pressure Oxygen & Nitrogen Charging Panels MK8 (71AS/3655-99-5685943) (Oxygen) & (71AS/3655-99-2519029) (Nitrogen).

            1. DAP 119F-2746-123: - Nitrogen Concentration Trolley (NCT) (71N/1730-01-503-1613).

RN Publications

            1. JSP 286- Defence Diving Manual: Pt 2 Vol 8 - Joint Service Adventure Training (JSAT) Diving

            1. BR 2000(89) - Compressed Gas System Design and Engineering Practices.

Joint Service Publications

            1. JSP 375 Part 2, Vol 1, Chapter 29: - Pressure Equipment and Systems.

            1. JSP 375 Part 2,Vol 3, Chapter 4: - JSP 375, Part 2 Vol 3 Chapter 4 Mechanical Systems - Boilers / Pressure Systems, Natural Gas / LPG Systems/ Medical Gas and Pipeline Systems and	Dental Air and Vacuum Systems.

            1. JSP 286- JSP 286 Defence Diving Manual.

            1. MAA01: Military Aviation Authority Regulatory Policy , MAA02 Military Aviation Authority Master Glossary, MAA03 Military Aviation Authority Regulatory Processes.

            1. DSA 02 - DMR Defence Diving Regulations.

            1. DSA03/DMR/DCOP 20- Guidance on MOD Military Diving Projects.

            1. DSA03/DMR/DCOP 22- Guidance on MOD Joint Service Sub-Aqua Diving Projects

MOD / RAF Forms

            1. RAF Form 3811- Application for Test.

            1. MOD Form 731 - MOD Form 731 - Equipment Conditioning Label.

            1. MOD Form 755F. - MOD Form 755F GSE Maintenance/Fault Work Order Log.

Health and Safety Executive

            1. HSE - L5 - The Control of Substances Hazardous to Health Regulations 2002. Approved Code of Practice and guidance, HSE L5 (6th edition, 2013).

            1. HSE Information Sheet No 9 - HSE Information Sheet, Diving Information Sheet No 9, Diver’s breathing gas standard and the frequency of examination and tests.

            1. HSE EH 40 - Workplace exposure limits Containing the list of workplace exposure limits for use with the Control of Substances Hazardous to Health Regulations (as amended).

# Annex A - Odour Assessment of Liquid Oxygen (LOx) and Liquid Nitrogen (LiN)

Principle. The liquefied oxygen or nitrogen is allowed to evaporate in a semi-enclosed receptacle and subjected to an olfactory assessment.

This is a subjective test.

Apparatus. See Table 6.A.1.

Table 6.A.1 - Apparatus and Consumables
Short Description of item	NSN
Beaker, Low Form, 400 ml, Borosilicate glass.	63C / 6640-12-1245668
Watch glass, 100 mm, Borosilicate glass.	63C / 6640-12-3658455
Filter Paper, 70 mm, Whatman No. 1.	63C / 6640-99-4887392

WARNING: Care should be taken as the evaporation of liquid oxygen can give rise to oxygen-enrichment in the immediate surroundings and cause increased fire risks. In these circumstances, consideration should be given to having a second person on hand to ensure the safety of the tester.

WARNING: Care should be taken as the evaporation of liquid nitrogen can give rise to oxygen-depletion in the immediate surroundings and cause asphyxiation or death. In these circumstances, consideration should be given to having a second person on hand to ensure the safety of the tester.

WARNING: Care should be taken to avoid cold burns and frost bite when handling liquid oxygen or nitrogen, or vessels in contact with liquefied gases.

WARNING: Suitable PPE, including gloves or gauntlets, and eye and face protection shall be used (refer to Part 2, Chap 2).

Quality Considerations. Ensure the tester(s) is not suffering from a cold, exposure to tobacco smoke, or any other condition that could adversely affect the tester’s ability to carry out the test.

Ensure that the tester washes her/his hands in plain unscented soap. Ensure that there are no other odours present, such as cosmetics, perfumes, contaminated clothing, etc. that could mask or adversely affect the test.

Ensure that the room or work area is free of any odours that could mask or adversely affect the test.

Method of Test for Odour. Pour approximately 100 ml of the liquid oxygen or nitrogen into a clean 400 ml beaker, rotate gently to cool the beaker down to cryogenic gas temperature and pour off the liquid.

Place a clean 70 mm diameter filter paper into the bottom of the beaker and add 200 ml of the liquid oxygen or nitrogen sample. Cover the beaker with a clean 100 mm diameter watch glass so as to prevent atmospheric constituents from being absorbed by the exposed liquid.

The convex face of the watch glass, i.e. the face shaped like the outside of a circle, should be in contact with the beaker and the concave face, i.e. the face shaped like the inside of a circle, should face upward.

Allow the liquid to evaporate to dryness in an area free from air currents and extraneous odours.

Remove the watch glass and check the odour of the beaker’s contents at frequent intervals until the accumulated frost on the outside of the beaker has completely melted. Any odour will be most noticeable when the beaker has warmed nearly to room temperature. Wherever possible the assessment should be carried out by more than one person.

Record the fact that this test has been carried out and note any odour.

# Annex B - Visual Examination of Liquid Oxygen (LOx) and Liquid Nitrogen (LiN)

Principle. The liquefied oxygen or liquid nitrogen is allowed to evaporate in a semi-enclosed receptacle, which is then visually inspected for the presence of suspended matter or particles. This is a subjective test.

Apparatus. Refer to Table 6.A.1.

Refer to Annex A para 3 to this chapter and observe all the WARNINGS given in that paragraph.

Visual examination and odour assessment are usually carried out at the same time.

Method of Visual Examination. Refer to Annex A para 7-9 to this chapter.

Examine the liquid oxygen or liquid nitrogen for the presence of suspended matter and visual impurities. Liquid oxygen is paramagnetic and has a pale blue colouration, liquid nitrogen is clear in colour.

Record the fact that this test has been carried out and note the presence of any suspended matter and/or visual impurities.

# Annex C - Odour Assessment of Gaseous Oxygen, Compressed Natural Breathing Air, or Diving Gases

      1. Principle. A sample of breathing gas is supplied into a semi-enclosed receptacle and subjected to an olfactory assessment. For high-pressure breathing oxygen, only, a dedicated test kit is used and the oxygen is breathed through a face mask.

      1. This is a subjective test.

WARNING: Care should be taken as gaseous oxygen, or Diving Gas mixtures containing more than 21% oxygen, can give rise to oxygen-enrichment in the immediate surroundings and cause increased fire risks. In these circumstances, consideration should be given to having a second person on hand to ensure the safety of the tester.

WARNING: Extreme Caution should be taken before assessing Diving Gas mixtures containing less than 21% oxygen. These gas mixtures may not support life when breathed at ambient pressure; they could give rise to oxygen-depletion in the immediate surroundings and generate increased risks of asphyxiation or death. In these circumstances, consideration should be given to having a second person on hand to ensure the safety of the tester.

WARNING: This test may be hazardous if attempts are made to carry out it directly from high-pressure cylinders; as gas under pressure can cause damage to the lungs and/or eyes. Consideration should be given to reducing the pressure of the supplied gas, to 2 bar (30 psi) or less, in the case of a free-flow supply, by means of a pressure regulator; and, to the provision of suitable eye and ear protection.

      1. Specialised test equipment is available for use with Breathing Oxygen cylinders and MCPs and this should be used in preference to the methodology given in Para 5 (refer also to Para 9), this provides a flow restricted to 15 litre/minute at 3.5 bar.

      1. Quality considerations: Refer to Annex A para 4-6 to this chapter.

      1. Procedure (excluding high-pressure Breathing Oxygen). A regulated flow of gas is directed into a clean, odour-free, beaker, and the gas subjected to an olfactory assessment using short breaths only. Wherever possible the assessment should be carried out by more than one person.

      1. The odour, if any, is rated as satisfactory or unsatisfactory.

      1. It should be borne in mind that gases may not always be odourless and a gas should be classified as satisfactory if it has a slight odour that can be easily tolerated for long periods.

      1. As part of this assessment it may help to give a brief description of any odour, preferably by reference to an understood characteristic, such as e.g. oily, acidic, musty, and sulphurous.

      1. Procedure (high-pressure Breathing Oxygen). This test is carried out in accordance with DAP 119L 0320 12, using the Type B, 300-bar, Test Kit, fitted with a NEVOC cylinder adapter (refer to Table 6.C.1). Both test kits are fitted with a facemask to facilitate the assessment of odour; and should be maintained and be operated in accordance with DAP 119L 0320 12.

Table 6.C.1 - High Pressure Oxygen Test Kit
Item Description	Publication	NSN
Type B, 300-bar, Test Kit, fitted with a NEVOC cylinder adapter	DAP 119L-0320-12	71BG / 6665-99-562-5580

      1. For further details regarding the availability of the Test Kit, please refer to the relevant Support Authority: AC PT.

      1. This equipment should not be used for gases other than breathing oxygen, especially not for non-breathing gases or low-oxygen content diving mixtures that may not support life when breathed at ambient pressure.

# Annex D - DE&S Oils Lubricants & Gases Nominated Test Laboratory

            1. Address and contact details:

Analytical Services Manager BOC Gases (David Baird)
BOC Gases
Analytical Services Department
Bawtry Road.
Brinsworth
Rotherham.
South Yorkshire
S60 5NT

Tel: 01709 842750
Email: asdgroup@boc.com

Units are advised that the laboratory operates only during normal office hours. However, the site is manned 24 hours a day so it is possible to make deliveries outside normal working hours. In the event an urgent delivery/sample analysis is required outside of normal office hours, units are to co-ordinate their arrangements with:

Chelsea Hallett
Supply Chain Co-ordinator OLG and Lab Equipment
Tel: +44 (0) 117 332 8663
Work Mob: 07867 254750
Email: chelsea.hallett102@teamleidos.mod.uk
Chelsea.Hallett102@teamleidos.r.mil.uk

The Nominated Test Laboratory participates in the NATO Aviator’s Breathing Oxygen (ABO) Correlation Program, refer to Para 6 to this Chapter.

MOD Form 3811- Application for Test or Calibration, is to be raised in triplicate for all gas samples that are to be analysed:

              1. One copy is to accompany the sample to the Team LEIDOS approved Lubricants & Gases Nominated Test Laboratory.

One copy is to be retained by the Unit.

One copy is to be sent to the Gas Technical Team Manager within DSFA.

All copies are to carry the same serial number that is to be recorded in a register of MOD Form 3811 held by the unit.

MOD Form 3811 is available as an electronic download from the Catalogue of Forms on the RAF Forms Index.

# Annex E - Compressed Natural Breathing Air (CNBA), for Diving Gases and Gas Mixtures

Annex Sponsor: Diving Standards Team – Superintendent Diving

CNBA in cylinders. When CNBA is supplied for diving applications, by a gas supply company, in cylinders and MCPs, it shall be procured against the requirements specified in Def Stan 68-284 or BS EN 12021.

When provided via the MOD gas supply contract each cylinder will be supplied with a Certificate of Conformity. Each cylinder or MCP will have a label indicating the gas use-by date. Users are to confirm the gas is within this shelf life. Additional testing is required as laid down in DSA03/DMR/DCOP 20 Regulation 6 to meet the requirements of HSE Diving Information Sheet 9 - Divers' breathing air standard and the frequency of tests.

CNBA from a compressor system, general requirements - Refer to para 65 to the chapter.

Compressor systems employed to produce CNBA fall within the scope of the Pressure Systems Safety Regulations 2000 (PSSR) (see JSP 375, Part 2, Vol 1 Chapter 29). In respect of CNBA, this includes a periodical check on the quality and the flow rate of the delivered air. Refer to Table 6.E.1 for periodicities and check points.

Frequency and Range of Testing. The frequency and range of quality testing shall be determined by a Risk Assessment. The assessor shall ensure that wherever a compressor is located, the quality of CNBA it supplies is not compromised by nearby contaminants. The quality of the CNBA produced shall be tested by a competent person at least once every three months, and more frequently when the quality of the CNBA supplied cannot be assured.

Table 6.E.1 - CNBA Periodicities and Check Points
Position of CNBA Test	Periodicity	By Whom
Mobile or Temporary Compressors	Before first use at any new location	Unit Staff using MoD supplied CNBA test Kit
All CNBA compressors and associated system	Following major overhaul / maintenance1,2 or breech which may have introduced contamination into the system.	Unit Staff using MoD supplied CNBA test Kit
Delivery Point of Charging Panels	3 Monthly	Unit Staff using MoD supplied CNBA test Kit or Independent Gaseous Analysis by an accredited Laboratory. / (Preferred Conformity Assessment Body (CAB) UKAS)
Compression Chamber Primary and Secondary supplies	3 Monthly	Unit Staff using MoD supplied CNBA test Kit or Independent Gaseous Analysis by an accredited Laboratory. / (Preferred Conformity Assessment Body (CAB) UKAS)
Delivery Point of Charging Panels	Annual	Unit Staff using MoD supplied CNBA test Kit or Independent Gaseous Analysis by an accredited Laboratory. / (Preferred Conformity Assessment Body (CAB) UKAS)
Compression Chamber Primary and Secondary supplies	Annual	Unit Staff using MoD supplied CNBA test Kit or Independent Gaseous Analysis by an accredited Laboratory. / (Preferred Conformity Assessment Body (CAB) UKAS)
Notes: / Additional testing may be required for ships and submarines and details can be found in BR 2000(89). / Extent of maintenance that requires subsequent ships staff or independent gas testing shall be directed by the Equipment Sponsor.

CNBA testing by unit staff may be carried out using the test equipment detailed in Part 2 Chap 6 112 – 125. Independent Test samples are to be sent for analysis to an accredited laboratory and tested using their accredited procedure to the relevant standard. Records of all testing carried out are to be kept.

Assessment of odour (refer to Annex C to this chapter).

CNBA for use in military diving equipment shall comply with the requirements of Def Stan 68-284.

CNBA used solely for Adventurous Training diving shall comply with the requirements of BS EN 12021. Procedures for the use of diving gases in the Adventurous Training diving are detailed in JSP 286 Pt 2: Guidance - Vol 8: Joint Service Adventurous Training (JSAT) Diving.

CNBA manufactured using approved diving plant, can be tested on location by trained competent personnel. This testing may be carried out using the test equipment detailed in Part 2, Chap 6 Table 6.6. Or test equipment to at least an equivalent specification approved for use by the responsible Equipment Sponsor. The frequency and range of testing shall be determined by a Risk Assessment. However, the quality of the CNBA produced shall be tested at least once every three months, and more frequently when the quality of the CNBA supplied cannot be assured. The assessor shall ensure that wherever a compressor is located, the quality of CNBA it supplies is not compromised by nearby contaminants; this is of particular concern where the CNBA supply is from mobile compressors.

Annual CNBA Sampling. On an annual basis, a sample of the CNBA produced by each diving plant shall be sent for analysis to a laboratory accredited to the latest edition of BS EN ISO/IEC 17025:2017

The competent person shall carry out an assessment of all test results to ensure that the CNBA remains fit for purpose and within specification - Refer to para 69 to this chapter.

Record Keeping - Refer to para 71 to this chapter.

Procedures for the use of diving gases in the Adventurous Training diving are in JSP 286 Pt 2: Guidance - Vol 8: Joint Service Adventurous Training (JSAT) Diving.

Diving gas sampling cylinders are available (refer to Para 121).

Diving gases and diving gas mixtures supplied in cylinders. This includes CNBA; oxygen for diving; specified mixtures of oxygen and nitrogen (Nitrox); specified mixtures of oxygen and helium (Heliox); or specified mixtures of oxygen, helium and nitrogen (Trimix). These gases are procured against the requirements specified in Defence Standard 68-284 for military diving and BS EN 12021 latest edition for Adventurous Training diving.

Each cylinder or MCP supplied via the MOD gas supply contract will have a label indicating the gas Use-By date. This is either five or ten years from the date of filling, depending on the product. Users are to confirm the gas is within the appropriate shelf life. A Certificate of Conformity is supplied with each cylinder or MCP. Testing is required as mandated in DSA03/DMR/DCOP 20 Guidance on MOD Military Diving Projects Regulation For further details refer to para 64.

CNBA manufactured using approved diving plant, by a trained competent person to produce Nitrox / Trimix diving gas by volumetric mixing with pure oxygen and/or helium, the CNBA shall comply with the requirements for oxygen enriched air specified in the latest edition of Def Stan 68-284 for military diving or BS EN 12021 for Adventurous Training

Some “diving gases” are available in the form of calibration mixtures, supplied with Certificates of Analysis, for verifying test equipment.

The use of diving gases and diving gas mixtures is controlled by written instructions and procedures issued by the MOD Superintendent of Diving, refer to Part 2, Chap 16, for further details. This includes a determination, by measurement, of the oxygen content of the diving gas / diving gas mixture.

Additional testing is required for diving gas mixtures as mandated in JSP 286 Pt 2: Guidance - Vol 8: Joint Service Adventurous Training (JSAT) Diving, to meet the requirements of HSE Diving Information No 9 – Breathing Gas Standard.

Where relevant, refer to Part 2, Chap 5, for filling of gas cylinders.

# Annex F - Marine Life Support, Marine Firefighting, Emergency Escape on Board Ships and Submarines

No Annex Sponsor - Information Only

            1. On board HM Ships and submarines, CNBA is produced by compressors and stored either in cylinders for bulk pressure storage vessels for the following applications:

Marine life support systems.

Firefighting.

Diving applications.

            1. CNBA is produced on boards HM Ships and Submarines using current in-service compressors, supplied by the relevant Project Team.

            1. Compressors installed on HM Ships produce compliant CNBA in accordance with the specifications in Para 65 .The test requirements of CNBA shall comply with BR 2000(89).

            1. Because of the finite (enclosed) atmosphere on HM Submarines, the CNBA quality standards are unachievable when compressing submarine atmosphere into CNBA cylinders. Allowable contamination limits for CNBA produced on HM Submarines is detailed in (BR0241 & BR1326, and DEF STAN 02-314 & 02-343). In service exemption / derogation for air quality / contamination limits is detailed in Annex B of Def Stan 02 -343 (INM /252/041 dated 23 Oct 2012).

# Annex G - Aviation Emergency Breathing Apparatus (BA)

No Annex Sponsor - Information Only

1.	CNBA in cylinders and / or supplied from in-service compressors. When CNBA is supplied for Short Term Air Supply System (STASS), & Passenger Short Term Air Supply System (PSTASS), by a gas supply company, in cylinders and MCPs; or supplied from an in service compressor, it shall be supplied against the requirements in Part 2, Chap 6, Para’s 63

PSTASS

2.	The maintenance and testing policies for STASS and PSTASS (including charging benches) shall comply with the relevant Air Publications managed by ACT.

3.	Where in-service compressors are used to provide CNBA for STASS & PSTASS; they shall be maintained by the Management Maintenance Organisation, refer to Part 2, Chap 6, Para 66.

4.	Where in-service compressors are used to provide CNBA for STASS & PSTASS; gas testing shall be carried out (refer to Part 2, Chap 6, Para’s 66-70) by a competent person / accredited Contactor.

            1. CNBA stored in STASS / PSTASS cylinders shall be defined as “in use”. The Project Team / Equipment Sponsor and Operating Authority who manage / operate STASS / PSTASS cylinders shall be responsible for CNBA air quality remaining in specification when stored in STASS / PSTASS cylinders.

            1. Record keeping of CNBA charges and results of CNBA testing shall be held by the respective SE workshop / QA department.

# Annex H - DFR Firefighting CNBA

Annex Sponsor - DFR-HQ -SCP-GM-SR

            1. CNBA in cylinders and / or supplied from in-service compressors. When CNBA is supplied for firefighting BA, by a gas supply company, in cylinders and MCPs; or supplied from an in service compressor, it shall be supplied against the requirements in Para 63 to this chapter.

            1. The maintenance and testing policies for firefighting BA (including charging benches) shall comply with maintenance publications sponsored by the relevant Project Team / Equipment Sponsor.

            1. Where in-service compressors are used to provide CNBA for firefighting BA; they shall be maintained by the Management Maintenance Organisation.

            1. Where in-service compressors are used to provide CNBA for firefighting BA; gas testing shall be carried out by a competent person / accredited Contactor.

            1. CNBA stored in firefighting BA cylinders shall be defined as “in use”. The Project Team / Equipment Sponsor and Operating Authority who manage / operate firefighting BA shall be responsible for CNBA air quality remaining in specification when stored in firefighting BA.

            1. Record keeping of CNBA charges and results of CNBA testing shall be held by the respective Line Management / QA department.

# Annex I - Workplace use CNBA

Annex Sponsor - TLB CESO for cascade to SME’s

      1. CNBA in cylinders and / or supplied from in-service compressors. When CNBA is supplied for workplace BA (paint spray shops, PMS bay, fuel tank access, etc.) by a gas supply company, in cylinders and MCPs; or supplied from an in service compressor, it shall be supplied against the requirements in Part 2 Para 63.

      1. The maintenance and testing policies for workplace BA (including charging benches) shall comply with maintenance publications sponsored by the relevant Project Team / Equipment Sponsor.

      1. Where in-service compressors are used to provide CNBA for workplace BA; they shall be maintained by the Management Maintenance Organisation.

      1. Where in-service compressors are used to provide CNBA for workplace BA ; gas testing shall be carried out by a competent person / accredited Contactor.

      1. CNBA stored in workplace BA cylinders shall be defined as “in use”. The Project Team / Equipment Sponsor and Operating Authority who manage / operate workplace BA shall be responsible for CNBA air quality remaining in specification when stored in workplace BA.

      1. CNBA supplied by compressors directly to in-line fed RPE shall be defined as “in use”. The Project Team / Equipment Sponsor and Operating Authority who manage / operate the in-line RPE shall be responsible for CNBA air quality remaining in specification at point of use, (i.e. the face mask).

      1. Record keeping of CNBA quality and results of CNBA testing shall be held by the respective Line Management / QA department.

# Annex J – Clarification on why Testing is Conducted

Annex Sponsor – DSFA Tech Gases Manager

Quality assurance and testing are key elements to ensure products are fit-for-purpose. Quality assurance is a process or set of processes which is used to measure and assure the quality of a product. Testing is the process of inspecting the product at various stages to keep defective items from reaching the end user.

For certain products, such as aviation oxygen and nitrogen, the quality of the gases is paramount to minimise any detrimental risk to life and equipment. Although BOC quality assurance provides a certain degree of confidence to Defence on the quality of the gases, but Defence want to further minimise the risk of defective products reaching end users by having targeted testing before Defence put these products to use.

The approach taken by Defence follows the classic Swiss-Cheese model. Each slice of cheese represents a barrier, any one of which is sufficient to prevent a hazard turning into consequences. Swiss-cheese theory works on the assumption that no single barrier is fool-proof. They all have failings or ‘holes’. A risk event can fall through these holes as negative consequences. BOC quality assurance is a slice of cheese in the Swiss-Cheese model. The gas testing is another and final slice of cheese in the same Swiss- Cheese model. Here we assume a risk event has fallen through the BOC quality assurance process. The gas testing is therefore put in place to manage the risk as far as is practically possible.

Risk management decisions are not always black or white. They depend on perceived likelihood of the risk and degree of the risk that you are prepared to accept. This may vary from case to case and person to person. In this case, the perceived likelihood of the risk is low thanks to the BOC quality assurance. Since the perceived likelihood of the risk is low, we are prepared to accept the risk with a less rigorous testing regime which picks out two cylinders from each pallet load to be tested before putting the cylinders to use. If the perceived likelihood of the risk is high, we may not readily accept the risk. To reduce the risk, we may impose a more rigorous testing regime which picks out more than two cylinders for testing. How many cylinders are picked out for testing depend on the level of risk you prepare to take?

We recognise that since only 2 cylinders from each pallet are tested, it would not mitigate the risk of defective cylinders reaching the end users completely. Only testing all cylinders from each pallet can completely mitigate the risk. Testing all cylinders is time consuming. Defence needs to strike a balance on the risk that it is prepared to accept and practicality.

Generally, defect manifests itself throughout the batch. This means most if not all cylinders from the same batch would be affected. If the cylinders in a pallet are from the same batch, random selecting 2 cylinders from the pallet would have a higher probability picking out a defective cylinder since more defective cylinders are among the pallet. It is under this scenario, testing is most effective. If you have 4 or more defective cylinders in a pallet of 15, randomly selecting 2 cylinders for testing would theoretically reduce the risk of defective cylinders reaching the end users by more than 47.62%.

Compare this with a scenario in which we have 15 randomly assembled cylinders in a pallet (as in the case for nitrogen cylinders). We assume one of these cylinders is defective. This scenario represents the most difficult case to screen out a defective cylinder. If we randomly pick out 2 cylinders from the pallet for testing, the probability that we have picked out the defective cylinder is 0.1333 (= 2 x 1/15) or 13.33%. In other words, we theoretically reduce the risk of defective cylinders reaching the end users by 13.33%. The risk reduction is small but significant.

# 7 - Handling and Use

Sponsor - DSFA Technical Gases Manager

## General

      1. This chapter details the general requirements and safety precautions necessary when handling, either manually or mechanically, and/or using gas cylinders. The handling and lifting of gas receptacles is a potentially hazardous operation; and the MOD policy is to avoid, wherever practicable, carrying out manual handling operations. All employees and line management are to take every precaution to ensure injury does not occur.

      1. Gas cylinders are generally heavy and are relatively unstable due to the base diameter to height ratio. Large cylinders can weigh over 100 kg when full and being tall and thin they are easily toppled over. In particular, when moving liquefied gas cylinders from the vertical position the centre of gravity will alter and this may affect the stability of the cylinder.

      1. Accidents can be caused by cylinder mishandling and unsafe storage. The destructive potential arising from the uncontrolled release of gas from a high-pressure cylinder can be considerable. It is essential that proper training and instruction is given to all personnel involved in gas cylinder handling. Gas cylinders are only to be handled and used by properly trained persons. Improper cylinder handling techniques can lead to injuries to the back, hands, feet and chest. Where there is a risk of injury, an assessment may indicate that the risk of injury is unavoidable. In such cases, wherever practicable, the operation should be mechanised; training shall be given and, as a minimum, appropriate handling aids provided.

      1. Defence Petroleum and Specialist Training Squadron Worthy Down provides a supply specialist training course for all logistics & supply personnel who are employed on compressed gas duties. Refer to Part 1 Chap 5.

      1. A suitable and sufficient risk assessment of the risk of injury from manually handling gas receptacles shall be carried out, in accordance with the Manual Handling Operations Regulations 1992, (refer to JSP 375, Part 2 Vol1, Chapter 8. A suitable and sufficient risk assessment of injury from manual handling gas receptacles shall be carried out in accordance with JSP 375 Part 2 Vol 1 Chapter 10 (Manual Operations Regulations 1992). Manual Handling training is required for all personnel who handle gas receptacles. A BCGA Publication – Guidance Note 3, the application of the manual handling operations regulations to gas cylinders – is available to assist in carrying out a risk assessment on manual handling.

Notes:
a.	There is a range of proprietary handling equipment available to assist in the handling of gas cylinders.
b.	It is a legal requirement that manual handling aids are regularly checked and maintained.
c.	BCGA Publications Guidance Note 3 – The application of the manual handling operation regulations to gas cylinders; and BCGA Code of Practice 18 are available to assist Line managers in carrying out a risk assessment on manual handling.

The use of lifting equipment and other work equipment used to support the storage and handling of gas cylinders, shall be subject to suitable and sufficient risk assessments by Line Managers, Assessors, and operators in accordance with the Provision and Use of Work Equipment Regulations 1992; and the Lifting Equipment Regulations 1998. (JSP 375, Part 1, Vol 2 Chapter 22 and 24 respectively).

All cylinders shall have their contents identified as defined in Part 2, Chap 3. Content identification labels are applied after filling, and the identification labels shall be present during transportation, delivery to user and during use. If the contents cannot be accurately identified the cylinder shall not be used, the cylinder shall be labelled as unserviceable and returned, in accordance with Defence Logistic Framework (DLF)

Gas cylinders shall not be used for anything other than the purpose for which they are designed for. Misuse could result in damage being caused to the cylinder or its valve, and could lead to leakage of hazardous gas or create a hazard during subsequent filling of the cylinder. Any cylinder or other gas receptacles which is known to have been misused shall be set aside and not issued for use or refilled; it shall be labelled as unserviceable and returned, in accordance with Defence Logistic Framework (DLF). The gas supplier and the Support Authority shall be notified so that the appropriate safety measures can be taken.

All personnel handling, lifting or using gas cylinders shall use the appropriate PPE (refer to Part 2, Chap 2).

Every effort is to be made to prevent contamination of the gas, particularly by preventing ingress via the valve outlet. New deliveries of gas cylinders will have the valve outlets blanked and/or will be protected by a shrink-wrap cover. All valve outlets shall be fitted with blanks at all times when not in use to help prevent the ingress of contamination. This applies to part-used cylinders and those that are nominally empty. Any external contamination of the cylinder or valve shall be removed. If contamination of the gas is suspected, or if any contamination is believed to have affected the properties of the cylinder or its fixtures and fittings shall be labelled as unserviceable and returned in accordance with the procedures detailed in Defence Logistic Framework (DLF).

Cylinder with a shrink wrap cover

Cylinder with a plastic cap cover

## Gas and Cylinder ‘Lifing’

Cylinder lifing. Before transporting, handling or use of a gas cylinder the operator shall check the cylinder is within its prescribed life. There are two distinct 'lifes' that need to be considered.

Mechanical life of the cylinder. All transportable gas cylinders are required to have an Inspection and Test on initial manufacture, and subsequently they are all required to have a Periodic Inspection and Test to ensure they remain serviceable for use. The date of the last Periodic Inspection and Test is stamp-marked on the neck of the cylinder. Cylinder test rings (two plastic coloured rings) are fitted around the neck of the cylinder to provide a quick, visual reference that shows when the cylinder is next due for a Periodic Inspection and Test (refer to Part 2 Chap 3 Annex A).

A transportable gas cylinder past its Periodic Inspection and Test date may continue in use at a static location (subject to its serviceability and any independent life on the gas contents). On expiry of their Periodic Inspection and Test life transportable gas cylinders may be transported only for purposes of returning them back to a place where the Periodic Inspection and Test will be carried out (return to the supplier/contractor). Cylinders do not have to be empty when transporting, the majority are not. As long as there is no obvious defect with the cylinder / valve it can be transported. It is recommended that all cylinders which have past their periodic inspection and test date are returned to the gas cylinder supplier and, as required, replaced with serviceable items.

Life of the gas within a cylinder. Certain gases are given a life. Depending on the gas type this typically ranges from 2 years to 10 years. This is indicated by the supplier using a label, attached to the shoulder or plastic collar of the cylinder. Once this life has expired the gas is no longer fit-for-purpose and the gas cylinder shall be returned, in accordance with Defence Logistic Framework (DLF)

Cylinder with a gas life date label

Corrosive gases. Cylinders containing corrosive gases are actively controlled by the gas supply company. Each cylinder is allocated an 'expiry' or 'return by' date at the time of filling. Typically, this will be three years. All units are to ensure cylinders are returned promptly to the gas supplier when the “return by” date has expired.

## Precautions and User Procedures

Safety Precautions when handling / using gas cylinders. Gas cylinders are only to be used for the transport and storage of gas. Always observe the following safety precautions:

              1. Use gas cylinders in a vertical position, unless they are specifically designed to be used otherwise. This is particularly important for liquefied gases such as LPG, carbon dioxide and acetylene.

All gas cylinders are to be securely restrained to prevent them from falling over. Gas cylinders, which are left in a gas cylinder trolley, are to be secured to an appropriate strong point to prevent the combined trolley and gas cylinder falling over.

If cylinders are leaning over in their pallet or storage bay, do not attempt to straighten them by yourself. Get help and make sure that you know what everyone else is doing to avoid trapping each other’s fingers or being hit by a falling cylinder.

Before connecting a gas cylinder to equipment, or pipe-work, make sure that the regulator and pipe-work are suitable for the type of gas and the inlet and outlet pressures being used. Always use an appropriate regulator with the	cylinder. Do not connect directly to the cylinder valve.

Do not remove valve guards, or any other permanent fittings, on a gas cylinder. If there is a requirement to remove fittings, then prior authorisation is to be obtained from the cylinder owner and the responsible Support Authority.

Wear the correct personal protective equipment when handling or using gas cylinders (refer to Part 2, Chap 2).

Gas cylinders are not to be used as rollers or supports.

Do not drop, roll or drag gas cylinders. A suitable hand truck, forklift truck or similar material handling device shall be used with the cylinder securely held by the device, especially for large or heavy cylinders. Caution shall be used to guard against dropping or permitting cylinders to violently strike against each other or other surfaces.

Do not move the cylinder with the valve open.

Cylinder valves are normally protected by a cap, or a guard/shroud. The user shall keep caps on cylinders at all times except when cylinders are connected to dispensing equipment. Replace the cap before returning to stores. Valve guards/shrouds are not to be removed by the user.

Note: Some cylinders have valves that are designed to withstand impact if the cylinder is dropped and therefore do not have guards/shrouds fitted.

Keep cylinders away from all sources of contamination, including flammables, corrosives and all fuel and lubricants. Never use oil or grease on a cylinder valve, it is dangerous. If the valve is tight, return the cylinder to the supplier and obtain a replacement. Do not use excessive force to open the valve.

Do not use a cylinder found to be leaking. If safe to do so, move the cylinder out-of-doors to a well-ventilated area and take the appropriate action to make the cylinder safe (refer to Part 1, Chap 6).

Cylinders shall not be placed where they become part of an electrical circuit. When gas cylinders are used in conjunction with electric welding, they shall not be used for earthing (grounding) of electrical equipment. Arc welding near gas cylinders is to be avoided. This precaution will prevent the cylinder from being arc-burned.

When using barrier creams, or other types of skin creams, avoid immersing skins with cream in oxygen rich environment. The cream my burn in an oxygen rich environment. In particular do not handle the oxygen cylinder valve and cylinder valve outlet, pressure regulator, etc. Use the appropriate clean PPE (refer to Part 2, Chap 2).

Check the compatibility of the gas against the materials used in the manufacture of the pressure equipment to which it will be connected (e.g. Regulators, gauges, hoses, etc). For example, oxygen cylinders are only to be connected to equipment that is specifically designed for oxygen service, acetylene cylinders are only to be connected to equipment that is specifically designed for acetylene service.

Never attempt to stop a falling cylinder. Get out of the way until the cylinder comes to rest.

Ensure that you read the gas Safety Data Sheet. Take time to understand the properties and hazards associated with the gas before handling or using it. If in doubt seek appropriate advice. Ensure you know what to do if an emergency situation develops (refer to Part 1, Chap 5).

Keep all gas cylinders within their safe temperature range. Typically, this is between – 20 °C to + 50 °C. Keep cylinders away from excessive heat sources. When gas cylinders, which are not part of the permanent equipment,	are being carried in vehicles or aircraft which are likely to be subjected to extremes of temperature e.g. medical cylinders for emergency response teams, those cylinders are to be removed from that platform until actually required for use.

Use in a well-ventilated area. Do not smoke or use direct heat on a cylinder. Keep away from any sources of ignition.

All valve outlets are to be fitted with blanks at all times when not in use to help prevent the ingress of contamination. This is particularly important for breathing gases, or specialist gases produced to a high specification. Ensure removed blanks are stowed in a safe place for re-use, or to prevent them becoming a hazard e.g. in the aircraft environment.

As far as is reasonably practical all gas cylinders are to be protected from potential damage when located in a hostile military environment. Any charged gas cylinder penetrated by a projectile, such as a bullet, will rupture	explosively, will release the gas contents into the immediate environment and will project fragments of the cylinder around the local area.

Before use procedure. Always carry out a before-use inspection on pressure equipment to ensure it is serviceable and appropriate for its intended task. This is to include:

  1. A visual examination of the cylinder and its attachments for obvious damage, security of any attachments, contamination and in general, fitness for purpose.

Note: Some gas cylinders, e.g. medical lightweight composite cylinders, have protective plastic liners around the body of the cylinder. Ensure the protective liner is complete, and that there is no obvious damage to the body of the cylinder beneath the protective liner.

  1. Always double check that the cylinder/gas is the right one for the intended use. Read the contents label. Check the colour code on the shoulder, (refer to Part 2, Chap 3).

  1. Where the gas cylinder is installed within equipment ensure that the correct size and type of gas cylinder is fitted, it is secure, it contains the correct gas for that equipment and that it complies in all respects with the appropriate equipment publication.

  1. Always read and comply with the appropriate Safety Data Sheet.

  1. Ensure the gas outlet connection is compatible with the equipment to which it will be fitted.

  1. Check the gas pressure/content is sufficient for the task. Some gas cylinders incorporate a contents gauge. Alternatively check using an appropriate regulator or pressure gauge.

  1. If applicable, ensure that the gas is within its expiry life. Typically, this will affect breathing, medical and some specialist gases. Refer to Part 2, Chap 3.

  1. Check the valve outlet is clear of any debris or contamination. Reject if excessively contaminated or there are any signs of oil. As necessary, wipe the cylinder valve outlet with a clean lint-free cloth. If a supply of oil-free compressed air or nitrogen is available this may be used to blow out any loose particles of dirt or residual moisture from the valve sockets. Alternatively, contamination can be removed by purging the valve outlet, through a process of cracking open and immediately closing the valve (sometimes referred to as “snifting”). When purging the valve outlet ensure that:

WARNING. Do not purge hydrogen as it may ignite spontaneously.

WARNING. Do not purge any toxic gases.

    1. Appropriate PPE including eye protection is worn; refer to Part 2, Chap 2.

    1. That there is no source of ignition in the vicinity.

    1. Stand clear of the gas stream and do not deflect the gas stream with the hand or face.

Where the gas cylinder is being carried in a purpose-built stowage bag, ensure that the bag is fully serviceable, the cylinder is installed within the bag correctly and that the bag and cylinder are secured within the platform. If the stowage bag is contaminated or unserviceable it is to be replaced.

In use procedure. Where gas cylinders are fitted to dedicated equipment the primary method of operation of the gas cylinder is to be in accordance with the appropriate equipment operating publication. In general, the following procedure is to be followed:

Operate the outlet valve using the valve hand-wheel or using the correct cylinder key.

Cylinder valves are always to be opened and closed slowly. Rapid movement can result in momentarily high pressures.

Check that the valve is not blocked and that the system is operating satisfactorily.

Monitor the cylinder, valve and pressure system being operated for gas leakage. Ensure that the valve does not leak in the open position e.g. by the use of leak detection fluid.

In the event of any leakage, then operation is to be stopped and the cylinder/ connections vented. The leak is to be rectified before proceeding. Leaks are not to be rectified whilst the system is pressurised.

Residual or excess gases are to be vented to a safe location, preferably outdoors in a well-ventilated area.

If work is temporarily stopped, always close the cylinder valve.

The operator is always to be in attendance when a gas cylinder is open and in use.

After use procedure. The following action is to be taken:

              1. Close the outlet valve. Ensure the cylinder is not leaking.

              1. Replace any protective covers, where provided, when a gas cylinder is not required for further use. Also, securely replace protective covers on all associated equipment once a cylinder has been disconnected. Avoid contamination of the system and the gas cylinder.

              1. Remove / disconnect any accessories e.g. regulators.

              1. Remove the cylinder key. Do not leave the cylinder key in the valve when	the cylinder is not in use.

              1. Clean off any contamination that may have occurred during use.

              1. If the cylinder is empty, identify it as such and return it.

              1. If the cylinder is unserviceable, follow the procedures in DLF.

              1. Return the cylinder to its correct stowage or store.

              1. Where the gas cylinder is being carried in a purpose-built stowage bag, ensure that the bag is fully serviceable. If the stowage bag is contaminated or unserviceable it is to be replaced.

Bowman radios. It has been identified that there is a risk that Bowman radios could generate a spark that might ignite flammable gases, particularly when used in areas of high ambient temperature.

WARNING. Flammable gases are not to be released from their receptacles unless all BOWMAN radio transmissions have been disabled within the safety distances detailed below.

All Bowman transmissions (except Personal Role Radio (PRR)) are to be disabled in the vicinity of flammable gases within the safety distances detailed below (this includes liquid oxygen storage and operational sites):

  1. HF Radios, within 70m.

  1. VHF radios, within 15m.

  1. UHF radios, within 15m.

## Handling

Handling and Use. Manual Handling. Wherever practicable, purpose designed trolleys should be used for moving cylinders. For moving over smooth floors, or for short distances, the ‘churning’ method may be used.

The churning method requires the use of both hands. One supports the cylinder whilst the other rotates the cylinder (away from the body). It requires the cylinder to be tilted slightly (again away from the body). The method takes some practice and if used should only be attempted on a firm, even surface.

Figure 7.1: Churning a cylinder

Manually raising a large cylinder from the horizontal position. Some cylinders are very heavy and before attempting to raise a cylinder manually, personnel are to ensure they have had appropriate manual handling training, that a valid written risk assessment is in place; and that they are wearing the required PPE. Be aware of your personal limitations before attempting to lift a cylinder. If necessary, use appropriate lifting equipment or get assistance. Avoid injury by using the correct lifting method when raising cylinders from the horizontal.

The BCGA (Technical Information Sheet 12: 2005) gives the following method:

  1. Foot position: hip width apart with one slightly in front of the other, astride the valve end of the cylinder.

  1. Bend the knees to lower your body. This will enable your thigh muscles to do most of the lifting.

  1. Ensure that the valve guard is secure then take a firm grip using both hands. Only lift using the guard if it has been designed for this purpose, otherwise grip the cylinder neck.

  1. Keep your back straight throughout its length. This does not mean it has to be vertical. Doing this will help to prevent a slipped disc. Pull your chin in so that your back is locked in a straight line and look in front rather than at the ground.

  1. Lift decisively with a smooth non-jerking motion. It is done initially by straightening the legs then following through with the arms at the same time walking forward until the cylinder is upright.

  1. Do not leave the upright cylinder free standing but move it to a safe storage area.

Figure 7.2: Lifting a cylinder from the horizontal.

Loading Pallets. Pallets are designed to securely hold a load of cylinders for the purpose of distribution or storage. Purposes built pallets have been designed to cater for compressed gas cylinders and globally there are a wide variety of pallet designs and types (refer to Annex A of this Chapter).

Pallets generally have three closed sides and include fork-lift slots in the base to facilitate movement by fork-lift truck. They include features, providing a secure location on vehicles, which are specifically designed to carry pallets. Cylinders are restrained by webbing straps and ratchets or ‘chain and dog’.

Small cylinders may be carried horizontally on shelving in pallets generally referred to as ‘wine rack’ types.

These guidelines are to be followed:

Load cylinders centrally within the pallet.

Pallets should preferably be loaded with cylinders of the same size, however if this is not practical:

    1. Ensure the load is stable.

    1. Place taller cylinders at the back of the pallet with shorter cylinders placed against the taller cylinders.

    1. Do not place small cylinders amongst larger cylinders. This can result in cylinders becoming dislodged during transit.

Cylinders are not to overhang the base of the pallet.

Part loads should be loaded, as far as practical, in a central position towards the rear of the pallet for reduced manual handling effort and stability of the pallet.

Cylinders are not to be placed on the top of another cylinder’s valve as this may cause damage to the valve.

Check pallets for serviceability before loading cylinders. Do not load cylinders into a pallet that has defective restraining straps or chains. Ensure the base is clear of debris and is not severely distorted.

Round bottom cylinders are not to be loaded into standard pallets. Do not ‘hide’ round-bottomed or unstable cylinders in the middle of a pallet.

Loading flat pallets. Best practice dictates that gas cylinders should be secured vertically within specially designed gas pallets using the affixed restraining straps. This is particularly so for cylinders containing liquefied gases, especially those with flammable contents (refer to Annex A of this Chapter).

Nitrogen cylinders on a partially filled pallet secured by a restraining strap.

Exceptionally gas cylinders may be palletised horizontally on wooden pallets. Only wooden pallets which are in a good condition e.g. no protruding nails, and which are free of contamination are to be used e.g. no oil, grease or tar contamination.

Gas cylinders that are laid flat on pallets are to be:

              1. Smaller than the pallet used. The cylinders are not to overhang the edges of the pallet.

              1. Adequately secured using appropriately sized wooden wedges.

              1. Banded using metal banding wire, applied through the nearest slats. Insert a protective barrier to avoid metal to metal contact with the cylinder.

              1. Spreaders are to be used to avoid cylinder to cylinder contact and to provide extra protection.

              1. All cylinder valves are to be protected using a valve-protection device e.g. a collar or a cap.

              1. Positioned such that the contents and hazardous goods labels on the cylinders remain visible at all times.

Ships Gas Cylinder Handling Trolley. Handling and lifting of gas cylinders onboard HM Ships and RFAs can be a hazardous activity involving the manual handling of potentially large, unwieldy, difficult-to-grasp gas cylinders often in confined spaces. A gas cylinder handling trolley which is capable of being lifted is available for use. Line Managers are to assure that the use of this trolley is considered as part of the control measures when carrying out the Risk Assessment for handling and/or lifting gas cylinders onboard HM Ships and RFAs.

Before each ships gas cylinder handling trolley is issued the manufacturer will carry out a load test from the lifting eye plates which will be recorded on the equipment data plate. The lifting eyes attached to the equipment are subject to examination / test against an examination scheme undertaken by a competent person. (Refer to JSP 375 Part 2, Vol 1,Chapter 24).

Records of examination and test are to be held within the lifting register.

Routine maintenance will consist of before-use and after-use inspections for serviceability for continued use.

The cylinder securing straps can be replaced. (see Annex A) In the event of any other fault which would make the equipment unsafe for further use the equipment is to be scrapped and a replacement obtained.

Mechanical Lifting

              1. Use suitable cradles, clamps or other effective means when lifting cylinders with a hoist or crane. Suitable platforms or pallets to hold the cylinders may also be used for lifting.

              1. Do not use valves, shrouds and caps for lifting cylinders unless they have been designed and manufactured for this purpose.

  1. Do not lift cylinders having a water capacity over 12 litres by using the valve protection device or magnets.

  1. Do not use ropes, chains or slings to suspend cylinders unless the manufacturer has installed appropriate lifting attachments such as lugs.

  1. Gas cylinders should not be raised or lowered on the forks of lift trucks unless adequate precautions are taken to prevent them from falling, i.e. use of suitable pallets with securing straps.

  1. When replacing cylinders in equipment, the cylinder replacement procedures detailed in the equipment publications are to be adhered to.

  1. Oil and grease are very hazardous when in contact with certain gases. Lifting devices contaminated with oil and grease is not to be used.

Note: Some smaller cylinders, such as medical cylinders, are designed to have a carrying handle, which also serves as the valve protection device. It is safe to carry such cylinders by such handles/shrouds.

## Leak Detection

Leak detection can be carried out using special equipment such as ‘sniffers’ or manometers. However, the simplest means of checking that an assembly is leak-proof is by coating the fittings with a surface-active liquid after the system is pressurised. Any leak is revealed by the formation of a bubble which is seen to expand.

The gas-tightness of the fittings of an assembly is never to be checked by the application of a low flame to gaskets and fittings.

Only approved leak detection fluids shall be used on gas cylinders. The use of certain chemicals can affect the integrity of cylinders and/or valves. Ammonia in association with oxygen and water, is very frequently responsible for stress corrosion cracking of copper-based alloys such as brass, which are often used for manufacturing cylinder valves. Also, consideration should be given to the likely presence of halide ions (usually chloride). Though not necessarily harmful to steel or brass surfaces, they do cause significant damage to aluminium alloy cylinders in the form of pitting corrosion. Further, the progressive accumulation of residues often in the form of a thin film of fatty acids, especially in the valve outlet, can cause an ignition in an oxygen environment.

Users shall carry out suitable risk assessments, with supportive evidence from gas supply contractors and equipment / platform sponsors / support authorities as appropriate, on the choice of leak detection fluid, taking into account the following:

Avoid using leak detection fluids which contain ammonia /	ammonium radicals.

Avoid using leak detection fluids that contain halide ions especially in conjunction with aluminium alloy cylinders.

Select leak detection fluids having a residue with an auto-ignition temperature (as measured using an oxygen environment), which is compatible with the intended application.

Carefully use the most diluted solution of a leak detection fluid consistent with the leak detection cycle.

General detergents or soapy water solutions are not to be used for leak detection.

After the check has been completed ensure the area is dry by wiping with a clean lint free cloth.

Table 7.1 - Recommended Leak Detection Fluids
Description	Quantity	Support Authority	Part No.	NSN
Teepol™ HB7	5 L receptacles	Team Leidos	11833457	71C/O443-6665-991335974 / BOC product code 11833457
Teepol™ HB7 hand spray	500 ml receptacles	Team Leidos	65220	BOC product code 65220

Teepol HB7 is provided ready for use (1% Teepol HB7 solution in distilled water).

Swagelok SNOOP® is NOT to be used as a leak detection fluid for use on gas cylinders and their fittings. Some receptacles have been found to contain ammonia

Team LEIDOS provide a cylinder valve leak tester (bubble tester) and a residual gas valve tester (prodder) use with for gas cylinders fitted with outlet valves containing positive residue pressure.

Table 7.2 - Valve Testers
Description	Contractor Part No.	NSN
Cylinder valve leak tester	13140053	71C/0443/8120-99-3974578
Residual gas valve tester	11857003	71C/O443/8120-99-9580541

## Discharging Gas

1. Contents of cylinders containing gases of any type shall not be discharged or vented to the atmosphere. On completion of use, the cylinder and its remaining contents shall be returned to the supplier for disposal.
## Bibliography

Lifting Operations and Lifting Equipment Regulations, 1998, (LOLER).

The Manual Handling Operations Regulations, 1992 (as amended).

Provision and Use of Work Equipment Regulations, 1992, (PUWER).

JSP 375 - Health and Safety Handbook.

BS ISO 11625 - Gas cylinders Safe Handling.

BCGA - Guidance Note GN 3, Safe Cylinder handling and the application of the manual handling operations regulations to gas cylinders

BCGA Technical Information Sheet TIS No 12: 2005 – Handle Gas Cylinders Safely.

The Merchant Shipping and Fishing Vessels (Lifting Operations and Lifting. Equipment) Regulations 2005.

# Annex A – Gas Storage Equipment

Description	Support Authority	NSN	Supplier Part No
Truck Hand (MOD Ship Trolley JN9022G)	Team LEIDOS	O443 / 3920-99-7259559	65481
Strap Securing (Straps for ratchet belt assembly for JN9022G)	Team LEIDOS	O443 / 3920-99-7512195	65483
Brass plug for BS 341 No 3 valve	Team LEIDOS	4730-99-8660-230	12090042
Plastic valve protector for the schraeder and fir tree connection on composite cylinders	Team LEIDOS	6515-99-9112-258	19305689
Single cylinder trolley (for K, N, L, W, J, & G cylinders)	Team LEIDOS	TBC	3623
Universal trolley (for F, T & G cylinders)	Team LEIDOS	TBC	TBC
Cylinder trolley (for J medical gas cylinders)	Team LEIDOS	6530-99-8994952	TBC
Cylinder trolley (for F, HX & ZX medical gas cylinders)	Team LEIDOS	6530-99-9882834	888816
Flame pack 50-cylinder trolley (for R, T, S, & J cylinders)	Team LEIDOS	TBC	3622
Small single cylinder trolley (for B, F, X, V, T, & Y cylinder)	Team LEIDOS	TBC	3619
Oxygen/Acetylene cylinder trolley (for N, W, & F cylinders)	Team LEIDOS	TBC	3620
Oxygen/Propane cylinder trolley (for N, W, & E cylinders)	Team LEIDOS	TBC	3621
Standard pallet	Team LEIDOS	3990-99-4370666	TBC
Pallet strap – Spanset ratchet part	Team LEIDOS	TBC	19316414
MOD Ratchet Belt Assembly for JN9022G	Team LEIDOS	O443 / 3920-99-7512195	65517
S/steel Ratchet for JN9022G	Team LEIDOS	TBC	65482

# 8 - Transportation

Chapter Sponsor DSA-DLSR-MTSR-Reg-DG-SO2

## Scope

      1. This chapter provides information on the regulations governing the transportation of Class 2 Dangerous Goods, including the military requirements for transportation by road, sea and air.

## General

2.	All gases and pressure receptacles, including gas cylinders, aerosols, tanks and Multiple Element Gas Containers (MEGC), are classified as dangerous goods and are therefore subject to transport of dangerous goods legislation as detailed within the bibliography. Dangerous Goods Manual (DGM) , Movement and Transport Safety Regulations are always to be consulted when transporting dangerous goods detailed within this publication.

The transportation of dangerous goods is regulated in order to prevent, as far as possible, accidents to persons or property and damage to the environment, the means of transport employed or to other goods.

Within the Carriage of Dangerous Goods and Use of Transportable Pressure Equipment (Amendment) Regulations 2011, gases are classified as Class 2. Substances of Class 2 are assigned to one of three divisions based on the primary hazard of the gas during transport.

Division 2.1	Flammable gases.

Division 2.2	Non-flammable, non-toxic gases.

Division 2.3	Toxic gases.

Only cylinders that have been designed to approve national & international standards and are also subject to periodic inspections that are carried out and approved by nationally recognised competent organisations can be transported. Further information on cylinder design standards & the authority for them to be refilled and transported can be found in BCGA Guidance Note 36 (GN 36); Guidance for the Use, Inspection & Transport of Cylinders with Various Design Codes.

Empty or partially filled gas cylinders. An empty, or partially filled, gas receptacles that has contained a dangerous substance is to be treated the same as a full receptacle and is therefore subject to all the relevant transport dangerous goods regulations. Only if adequate measures have been taken to nullify any hazard may the container be treated as non-hazardous.

Empty cylinders which have been processed (purged)as directed may be treated as non-hazardous, however all such cylinders shall be certified as ‘empty’ by a competent person.

Empty cylinders that previously contained a UN Class 2.2 gas, with a residual gauge pressure of less than 2.0 bar (200 kPa) at 20°C, and if the gas is not a liquefied or a refrigerated liquefied gas, may also be treated as non-hazardous goods.

Precautions transporting gas containers

  1. Fit suitable protective valve caps and covers to cylinders, when necessary, before transporting. Caps and covers help prevent moisture and dirt from gathering in the valve of the cylinder, in addition to providing protection during transport

  1. Securely stow gas cylinders to prevent them from moving, falling or overturning. This is normally in the vertical position, unless instructions for transport state otherwise. Wherever practical, use suitable pallets, which will assist in loading/unloading and securing the load (refer to Part 2, Chap 7).

  1. Disconnect regulators and hoses from cylinders whenever practicable.

  1. Do NOT let gas cylinders project beyond the sides or end of a vehicle (e.g. fork-lift trucks).

  1. Ensure gas cylinders are clearly marked to show their contents (including their UN Number) and the danger signs associated with their contents. All gas containers are to have the precautionary label fitted (refer to Part 2, Chap 3).

  1. All vehicles used to transport gas containers are to be well ventilated, toxic gases are not to be carried in a closed vehicle unless it is specifically designed for that purpose.

  1. It may be necessary to take special measures with certain types and quantities of compressed gases and fluids in order to ensure their safe carriage. Seek advice if unsure.

  1. Gas cylinders that have been exposed to fire shall not be shipped if they still contain gas under pressure. Seek advice from Team LEIDOS Lubricants and Gases Team or the appropriate Support Authority. Attach a suitably annotated Equipment Conditioning Label (e.g. MOD Form 731) to the cylinder.

  1. If a cylinder or valve is noticeably damaged or corroded, seek advice from Team LEIDOS Oils, Lubricants and Gases team or the appropriate Support Authority. Any other damage that might impair the safety of the cylinder during use or transportation shall be called to the attention of the Team LEIDOS Lubricants and Gases Team or the appropriate Support Authority before the return of the cylinder. Attach a suitably annotated Equipment Conditioning Label (e.g. MOD Form 731) to the cylinder (refer to Part 2 Chap’s 6 & 7).

Training. All personnel involved in the transportation of dangerous goods are to have received appropriate training commensurate with their duties.

Defence Supply Chain Operations and Movements. Defence Supply Chain Operations and Movements (DSCOM) provides Defence and other authorised users with agreed transport and movements services world-wide in peace, crisis and war in order to support current and future UK military capability. It is operationally focused and has formal responsibility for providing PJHQ with a single DE&S operational focus for mounting and sustaining operations. Within DSCOM the Movement Operations (Mov Ops) Division process, allocate and manage bids for freight movement by road, rail, sea and air to support UK Forces worldwide. The Defence Movements and Transport Branch is responsible for the Defence Policy for Hazardous Material and dangerous Goods.

Net Quantity Air Transport. The net quantity of gas shall be declared on the transport document. The net quantity is the net mass of the gas excluding the cylinder or containment vessel, shown in kilograms (kg).

Net Quantity Surface Transport. The net quantity of gas shall be declared on the transport document. The net quantity shall be declared as follows:

  1. For liquefied gases, refrigerated liquefied gases and dissolved gases, net mass in kilograms (kg).

  1. For compressed gases and absorbed gases, the water capacity of the receptacle in liters (l).

      1. Water capacity is stamp marked on the cylinder (Part 2 Chap 3 Annex B).

Note: Mass is commonly referred to as weight in everyday use and may be interchanged with weight in this context. Refer to Annex B for some worked examples.

## Inspection and Testing of Gas Cylinders

Periodic inspection and test. All refillable gas cylinders are subject to a periodic inspection and test. A refillable gas cylinder past its periodic inspection and test date may continue in use at a static location (subject to its serviceability and any independent life on the gas contents). Gas cylinders are not allowed to be filled after they become due for their periodic inspection and test but may be transported after the expiry of the time-limit for purposes of performing inspection or disposal, including the intermediate carriage operations. Units returning expired cylinders are to assess cylinders for any potential risk prior to transportation. Units are to seek advice from Team LEIDOS Oils, Lubricants and Gases team if they have any safety concerns.

15.	Units that hold deployment stocks are to conduct management checks to ensure cylinders remain in date for the duration of the deployment. UK Depots are not to consign gas cylinder overseas with less than 1 year remaining on the gas life (if applicable) and periodic inspection and test. See Pt 2 Chap 10 Para 20 for details.

16.	Cylinders do not have to be empty when transporting, the majority are not. Provided there are no obvious defects which could make it unsafe a cylinder can be transported. If in doubt, consult Team LEIDOS Oils, Lubricants and Gases team or the appropriate Support Authority.

## Transportation by Road

All Defence vehicles and their drivers are to comply with the requirement of DGM. All vehicles and their drivers are to comply with ADR.

DGM and ADR detail specific requirements for all vehicles carrying dangerous goods, including:

The suitability of the vehicle.

Identification marking.

Driver training.

The carriage of additional safety equipment.

The carriage of documentation relating to the dangerous goods being transported. This includes Instructions in Writing that are provided through the Movement and Transport Safety Regulator's Homepage.

The ADR regulations apply to everyone carrying gas containers in the course of their work. Exemptions are:

Loads that are under the exemption limits.

When private individuals carry dangerous goods, which are packaged for retail sale and intended for personal use (e.g. transporting a single cylinder of LPG for use on a home barbecue).

Note: Details of the exemption limits are at Annex A to this Chapter

High Consequence Dangerous Goods. The current edition of ADR and the Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations imposed new security requirements on the carriage of dangerous goods, covering: consignment; security of sites where they are stored during transit; and training of those involved. More stringent requirements apply to a subclass of dangerous goods known as High Consequence Dangerous Goods. Obvious examples of High Consequence Dangerous Goods are ammunition, explosives and flammable liquids in bulk. This group also includes certain gases in Class 2, Division 2.1 & 2.3. See DGM for more detailed information.

## Transportation by Sea

All dangerous goods transported by sea are to comply with the regulations within the International Maritime Dangerous Goods (IMDG) Code IMDG.

## Transportation by Air

All Class 2 dangerous goods transported by air are to comply with the International Air Transport Association (IATA) Dangerous Goods Regulations. Where there is a requirement for specific exemptions for military equipment then they are to comply with the requirements of DGM.

The shipper must specifically verify under IATA clause 5.2.0.5 that the filled cylinder is not leaking; and under IATA clause 5.2.0.13 cylinders cannot be offered for air transportation that are:

Leaking.

Damaged to such an extent that the integrity may be affected.

Unless it has been examined and found to be in good working order.

Unless the required certification, retest and filling markings are legible.

## Reporting Accidents / Incidents

Accidents / incidents when transporting dangerous goods. All accidents / incidents involving the transportation of dangerous goods are to be reported. Follow the procedures detailed in DGM (also refer to Part 1, Chap 4).

## Bibliography

      1. ADR: Agreement for the International Carriage of Dangerous goods by Road Goods by Road.

      1. RID : Regulations Concerning the International Carriage of Dangerous Goods By Rail.

      1. IATA: The International Air Transport Association (IATA) Dangerous Goods Regulations.

      1. IMDG: The International Maritime Dangerous Goods (IMDG) Code.

      1. Uk Statutory Instruments 2009: UK Statutory Instruments, 2009, No. 1348, The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations 2009

      1. JSP 515: The MOD Hazardous Stores Information System

      1. DSA03-DLSR Movement and Transport Safety Regulations – Dangerous Goods Manual.

# Annex A - Transportation by Road - ADR Loads Exemption Limits
(ADR Road - ADR 1.1.3.2. (c), Rail - RID 1.1.3.2. (c), Sea - IMDG Code 2.2.2.5, Air - IATA DGRs 3.2.2.4.1)

            1. All gas receptacles have a number of transport units associated with the capacity of the cylinder or the amount of gas they carry. There is a threshold below which certain basic legal safety regulations apply, above this threshold, the full ADR legislation applies. All gases have been classified by ADR into three of the five transport categories, i.e. categories 1 to 3, relating directly to the hazard diamonds for each product; plus transport category 4 which includes empty uncleaned receptacles which previously contained dangerous goods.

  1. Road - ADR 1.1.3.2.(c), Rail - RID 1.1.3.2.(c), Gases of Groups A and O (according to 2.2.2.1), if the pressure of the gas in the receptacle or tank at a temperature of 20 °C does not exceed 200 kPa (2 bar) and if the gas is not a liquefied or a refrigerated liquefied gas. This includes every kind of receptacle or tank, e.g. also parts of machinery and apparatus.

  1. Sea - IMDG Code 2.2.2.5 Gases of class 2.2 are not subject to the provisions of this code if they are transported at a pressure of less than 200 kPa at 20 °C and are not liquefied or refrigerated liquefied gases.

  1. Air – IATA DGRs 3.2.2.4.1 Gases of Division 2.2, are not subject to these Regulations if they are transported at a pressure of less than 200 kPa at 20 °C and are not liquefied or refrigerated liquefied gases

            1. There are no exemptions for small receptacles.

            1. How to calculate Transport Units. The regulations require different sizes to be added together, some in litres of water capacity and some in kilograms. These values are referred to as Transport Units.

            1. Compressed gases are measured in litre water capacity (e.g. Oxygen, Nitrogen).

            1. Liquefied gases and dissolved compressed gases (such as ACETYLENE, DISSOLVED) are measured in kilograms (e.g. Refrigerant R134a, Acetylene, CO2).

            1. The calculation and threshold limit depend on whether the customer is transporting:

A load containing one transport category.

A mixed load containing gases with multiple products of different categories.

Table 8.A.1 - The transport calculation and threshold limits for loads containing one transport category.
Transport Unit Limit / litre / kg	Gas	Classification
20	Toxic gases	Class 2.3
333	Flammable gases	Class 2.1
1000	Asphyxiates and Oxidants	Class 2.2 & 5.1
Unlimited	Empty receptacles
Note: For AMMONIA, ANHYDROUS (UN 1005) and CHLORINE (UN 1017) (both Class 2.3) the limit is to 50 Transport Units instead of 20.

            1. Transport units per receptacles x number of receptacles = Total load Transport Units.

Example calculation:

Load to be carried

1 x receptacles of R22, net weight 12 kg

3 x receptacles of R134a, net weight 65 kg per receptacles

2 x receptacles of R410A, net weight 24 kg per receptacles

All gases are classed as ‘Class 2.2’ so load is not mixed.

All three types of cylinders are liquefied gases (measure in kg)

R22; 12 x 1 = 12 Transport Units

R134a; 65 x 3 = 195 Transport Units

R410A; 24 x 2 = 48 Transport Units

Total; = 255 Transport Units
            1. Conclusion. This load is less than 1000 Transport Units allowed for a Class 2.2 and is not therefore subject to the full ADR regulations.

            1. For a mixed load containing gases with multiple products of different categories. Each category of gas carried has an associated calculation. Calculation must be performed for all individual categories of gases; the transport units for each category must then be added together.

            1. There are five steps.

Calculate the toxic gas Transport Units. (Transport Units per receptacles) x (number of receptacles) x 50 = T Transport Units.

For AMMONIA, ANHYDROUS and CHLORINE the calculation is :( Transport Units per receptacles) x (number of receptacles) x 20 = T Transport Units.

Calculate the flammable gas Transport Units (Transport Units per receptacles) x (number of receptacles) x 3 = F Transport Units.

Calculate the asphyxiant / oxidant gas Transport Units (Transport Units per receptacles) x (number of receptacles) = A Transport Units.

Add the three values together to acquire Transport Units for total load T Transport Units + F Transport Units + A Transport Units = Total Transport Units for mixed load.

Determine whether your load is above or below the threshold. If the load is above 1000 Transport Units then the ADR regulations must be observed in full.

Example calculation:
Load to be carried:
2 x Acetylene receptacles, liquid weight 10 kg per receptacles. Acetylene is a dissolved compressed gas and is measured in kg. (Class 2.1)

2 x Oxygen receptacles, water capacity 47 litres per receptacles
Oxygen is a compressed gas and is measured by receptacles water capacity, Litres (Class 2.2)
As these receptacles fall into different class categories, this load is mixed.
Acetylene, dissolved (10 kg = 10 Transport Units)
10 Transport Units x 2 receptacles x 3 = 60 Transport Units
Oxygen (Water Capacity = 47 litres = 47 Transport Units)
47 Transport Units x 2 receptacles = 94 Transport units
Total = 154 transport Units
            1. Conclusion. This load is less than 1000 Transport Units allowed for a mixed load and is not therefore subject to the full ADR regulations.

# Annex B – Net Quantity for Transport

Given gross mass	Note: / Tare mass is stamp marked on the cylinder (refer to JSP 319 Pt 2 Chap 3 Annex A). It is 28kg for BOC Acetylene J-size cylinder. / Gross mass, or sometime referred to as total mass, may be provided on labels used in gas cylinders. This is stated as 31kg on the label.
	Note: / Tare mass is stamp marked on the cylinder (refer to JSP 319 Pt 2 Chap 3 Annex A). It is 65kg for Industrial BOC Oxygen W-size cylinder. / Gross mass, or sometime referred to as total mass, may be provided on labels used in gas cylinders. This is stated as 80kg on the label.

Given gas volume		Note: / The gas volume may be provided on labels used in gas cylinders. This is stated as 7.0Sm3 (7.0 standard cubic meter) on the label, and is equivalent to 7000L. / Molecular weight of Acetylene is 26.04g/mol. Refer to Table 8.B.1.
		Note: / The gas volume may be provided on labels used in gas cylinders. This is stated as 7.6Sm3 (7.6 standard cubic meter) on the label, and is equivalent to 7600L. / Molecular weight of Oxygen is 32.00g/mol. Refer to Table 8.B.1.
Given cylinder pressure	Note: / Fill pressure may be provided on labels used in gas cylinders. If it is not provided, you may confirm the cylinder pressure using a pressure gauge. The cylinder pressure is assumed to be 300bar in this example. / The cylinder volume expressed in terms of water capacity in litres (L) is stamp marked on the cylinder (refer to JSP 319 Pt 2 Chap 3 Annex A). The cylinder water capacity is assumed to be 50L in this example. / Molecular weight of Nitrogen is 28.01g/mol. Refer to Table 8.B.1. / This calculation is only applicable to compressed gases. It is not valid for liquefied gases, refrigerated liquefied gases and dissolved gases.

Table 8.B.1 - Molecular weight of common gases.
Gas	Molecular Weight (g/mol)
Acetylene (C2H2)	26.04
Air	28.97
Argon (Ar)	39.95
Carbon Dioxide (CO2)	44.01
Carbon Monoxide (CO)	28.01
Helium (He)	4.00
Hydrogen (H2)	2.02
Nitrogen (N2)	28.01
Oxygen (O2)	32.00

# 9 - Gas Cylinder Storage

Sponsor - DSFA Technical Gases Manager

## Scope

This chapter provides information on the safe storage of gas cylinders. A gas cylinder storage compound is defined as a segregated area for the storage of gas cylinders that are held on a centralised / station account. It provides guidance on the physical attributes and requirements of both Gas and LPG cylinder compounds, for outdoor and indoor storage. This Chapter also highlights the hazards and the potential risks involved in storing gas cylinders and should therefore be read in conjunction with other Chapters within this JSP.

This chapter is not intended to be applied to the following:

Gas cylinders that have been issued to a user account and are in-use at the user’s location (refer to Part 2, Chap 7).

Storage of radioactive gases (refer to JSP 375 and JSP 392).

Static gas cylinder storage systems permanently connected for use; refer to respective Equipment / Platform publication.

“Carriage” as defined by ADR including intermediate temporary storage and cylinders that have been issued with transport documents.

Cryogenic liquids (refer to Part 2, Chap 11 and 12).

Bulk LPG storage vessels (refer to Part 2 Chap 19).

## Health, Safety, Environmental and Security Arrangements

Gas cylinders are potential Health, Safety, Environmental and Security risks; as such, gas cylinders are to be accounted for and actively managed whilst in a gas cylinder store.

Main Hazards. The major hazards associated with the storage of compressed gas cylinders are:

Ruptured Cylinder / valve resulting in missile effect of cylinder (refer to Part 2, Chap 1).

Cylinders are heavy and unstable – personnel crush injuries (refer to Part 2, Chap 7).

Uncontrolled high pressure gas releases -personnel injection injuries / eye injuries (refer to Part 2 Chap 7).

Uncontrolled high pressure gas releases - gas properties (Toxic, asphyxiant, oxidant, flammable, corrosive, global warming and ozone depleting potential) (see Part 2, Chap 1).

Gases may be classified with “hazard labels” (diamond hazard labels) iaw UN recommendations on the Transport of DG, and can identify more than one hazard, i.e. a primary hazard and secondary hazard(s). This does not affect the requirements for storage, which is based on the primary hazard, but may give rise to additional secondary hazards in the case of an unintended discharge of gas. (See ADR, Vol 1, Part 3; and JSP 319, Part 2, Chap 3). Gas cylinders of the same gas or the same hazard category shall be grouped together, e.g. flammable, toxic, oxidising, or corrosive (refer to Part 2, Chap 3).

Gas Cylinder Failure. Refer to Part 1 Chap 4 for the reporting of incidents/accidents associated with gas cylinders and uncontrolled gas releases.

Ozone Depleting Substances / Florinated Greenhouse Gases (F-gases). Refer to Part 1, Chap 4; Part 2, Chap 14 and JSP 418, Vol 2, Leaflet 5 - 7 for the restrictions and reporting on discharges of F-gases and Ozone Depleting Substances.

Risk Assessments. See Part 2, Chap 1 for gas systems risk assessments.

Leak Procedures. Before a site may be used for storing compressed gas cylinders, written SOPs for dealing with gas leaks and escapes shall be available for all personnel working on the site.

Training. The storage and handling of gas cylinders is to be carried out only by appropriately trained personnel; and will normally require the provision of suitable handling equipment (refer to Part 1, Chap 5 - Training; and Part 2, Chap 7 – Handling and Use).

PPE. The appropriate PPE shall be worn when handling gas cylinders or entering a gas cylinder storage area (refer to Part 2, Chap 2).

Bowman radios. It has been identified that there is a risk that Bowman radios could generate a spark that might ignite flammable gases, particularly when used in areas of high ambient temperature (refer to Annex B of this Chapter).

WARNING. Flammable gases are not to be released from their receptacles unless all BOWMAN radio transmissions have been disabled within the appropriate safety distances (see Annex B of this Chapter).

Fire / Emergencies. All gas cylinder storage sites are a potential fire / hazard risk (refer to Part 1, Chap 6). The DFRMO shall be informed and included in the initial setting up and siting of a gas cylinder store and its future management.

Storage of certain gases / classes of gases will have consequences in an emergency (refer to Part 1, Chap 6); this shall be considered during site selection.

## Outdoor Gas Cylinder Storage Compounds - Siting

Low Lying Areas. The storage locations of liquefied gases and heavier than air compressed gases, e.g. argon, carbon dioxide, LPG, etc, should take into consideration the dangers of gas seepage into drains, basements, manhole covers, cable ducts, etc. Storage of such gas cylinders in low lying areas of land may hinder the safe dispersal of any leakages. Conversely, gas cylinders stored in relatively low-lying areas may be susceptible to contamination from adjacent areas, such as run-offs from higher ground, sewage, effluent, fuel and oil spills, etc.

Confined Spaces. Gas cylinders shall not be stored in confined spaces. Any confined spaces adjacent to gas cylinder storage facilities that could be affected by a build-up of gas from leaks, or escapes, may fall with the scope of the Confined Spaces Regulations 1997; and shall be subjected to a written risk assessment (refer to JSP 375).

Explosives. Gas cylinders shall not be stored within an explosives area (PEZ). Exceptionally; should it be necessary; gas cylinders shall only be stored in the vicinity of explosives in accordance with the Quality Distances and Licensing Criteria procedures, see DSA 03 - OME Part 2 - Defence Code of Practice and Guidance Material for In-Service and Operational Safety Management of OME.

Electromagnetic Radiation. Radio and radar transmitters can produce an explosion hazard when sited close to some compressed or liquefied gas cylinders. However, because of the huge variance in transmitter strengths, frequencies, etc, it is not possible to include specific safety distances in this document. The hazards caused by high-powered radars can extend to several hundred metres and it is the responsibility of the unit Maintenance Management Organisation, with the managers of the radiating source and the gas cylinder storage facility who shall ensure that sensible safe distances are imposed.

Overhead Power Cables. Gas cylinders shall not be located directly beneath electricity power cables, including telephone cables. For cables operating at a voltage less than 1.0 kV, gas cylinders should be sited at least 1.5 m from a line drawn vertically downwards from the power cables. For cables operating at a voltage of 1.0 kV or greater, the distance shall be increased to 10 m. These distances shall be increased where the presence of the overhead cable could constitute a danger to users of the gas cylinder store, loading vehicles, or personnel.

Electrical Wiring / Underground Cables. Gas cylinder storage areas shall not be built on top of electrical cables. Electrical cables shall not be routed through the area. Where electricity cables are necessary, such as for lighting, they shall be maintained in a good condition and shall be to an appropriate standard.

Thermal Radiation. Consideration shall be given to the proximity of the gas cylinder storage area boundaries to other processes and equipment where there is the potential for a fire or explosion hazard. Precautions such as increased separation distances and properly designed fire or thermal radiation barriers are to be employed whenever such risks are high (refer to Annex B to ths Chapter).

## Outdoor Gas Cylinder Storage Compounds - Construction and Layout

Construction Materials. Gas cylinder storage facilities shall be constructed of non-combustible materials in accordance with current building design standards.

Within permanent gas cylinder storage facilities, the floor shall be flat and constructed of concrete or other non-combustible, non-porous material. All floor surfaces of the gas cylinder storage area shall be constructed so that they can be maintained clean. The floor shall be laid to a slight fall, and/or provided with suitable drainage, to prevent the accumulation of water.

Floors and drainage. All gas cylinder storage facilities are to be built on hard standings. Where the construction of hard standing is not appropriate eg Ops and exercises, the ground must be firm, well drained and of sufficient strength to support the weight of the cylinders, pallets and mechanical aids.

The drainage shall be such that any product spill is directed to a low risk area. The drainage system shall be designed to prevent spills or contaminated water entering surface water drains, or other controlled drainage or watercourses.

Protection against the Elements. Some gas cylinders, particularly those containing liquefied gases, are susceptible to extremes of temperature, both high and low temperatures; and in these cases, they are to be afforded protection from effects of direct sun light. Protection may also be needed from the elements, e.g. in desert conditions driving sand can have an adverse effect on protective finishes, warning labels; and cause contamination to gas cylinder valves and outlets.

In external storage areas, where necessary, gas cylinders are to be covered to protect against the effects of strong sunlight and/or to afford some protection against the weather and against corrosion. Any roof shall be designed with vents to prevent the accumulation of lighter-than-air gases in the roof-space.

In temperate climates, it is only necessary to protect certain cylinders containing liquefied gases, such as carbon dioxide, anhydrous ammonia and acetylene. For LPG refer to Chapter 17 to this JSP. In tropical climates all gas cylinders (in particular those containing acetylene and the liquefied gases) should, wherever possible, be protected from direct sunlight with due regard to provision of adequate ventilation over and around the gas cylinders. Where locally made covers are employed, they must be manufactured from white fire-resistant material to reduce the temperature produced by the sun's rays.

Partitions and Barriers. In some cases, the use of physical partitions or barriers may reduce the required separation distances. However, any cylinders stored adjacent to a partition are to be smaller than the partition (i.e. shorter, so that they are protected by the partition). Such partitions should be rated to provide fire resistance of at least 60 minutes; and shall not measure less than 2 m in height. Normally, partitions will be constructed of unperforated brick or concrete but other materials with equivalent or better properties may be used. However, some structures such as earth banks will require a greater thickness to provide equivalent effectiveness. Refer to Annex B for example.

DSEAR. A specific suitable and sufficient risk assessment is required under DSEAR for all gases that are within the workplace under pressure. The extent of the DSEAR risk assessment is dependent upon the flammability, oxidising, or corrosive properties of the gases and the risk of explosion, or the potential for structural damage, for example, if these gases are released to the atmosphere. When gases under pressure are in the workplace and no flammable, oxidising or corrosive risks exists, then the DSEAR risk assessment can record this and be completed. Employers need take no additional action to comply with DSEAR. The requirements of the Health and Safety at Work etc. Act and the Management of Health and Safety at Work Regulations, etc., mandate the need to carry out risk assessment and have arrangements in place for the general safe use of gases.

When flammable, oxidising or corrosive gasses are in the workplace the Employer is responsible for ensuring a comprehensive DSEAR risk assessment is carried out and documented. A suitable and sufficient task orientated workplace risk assessment, including elements pertinent to DSEAR, shall be carried out for all activities, including equipment selection and maintenance. For further guidance, refer to BCGA Guidance Note 13 section 4 and 5

Precautions shall be taken to ensure that no electrical current can reach the gas cylinders; steel floor inserts, structural members, and metal surfaces that can carry earth-return currents. This may require the provision of earthing rods or plates.

Based on on-site risk assessments; precautions may need to be taken to ensure that the facility including fencing, gates, tanks, and all pipe work is adequately protected against static electricity. This shall be in accordance with PD CLC/TR 60079-32-1:2018 Explosive atmospheres, electrostatic hazards, guidance.

All metal fitments in the facility, including fencing, gates, tanks and all pipe work, shall be adequately earthed. This shall be in accordance with BS 7430.

Lighting and other electrical equipment. Adequate and appropriate lighting shall be provided to assist in the security of the site; and in the identification of gas cylinder contents. The light source used shall give suitable colour rendering to enable colour labelling to be easily recognised by persons with normal colour vision.

Lightning protection. Lightning protection for compressed gas cylinder compounds shall be considered as part of the design risk assessment by the site owner. Where a lightning protection system is required, it shall comply with BS EN 62305 series.

Ventilation. All gas cylinder storage areas shall be constructed so as to provide a high standard of natural ventilation. The minimum for a store to be considered ‘outdoors’ may consist of up to three adjacent solid sides, with a roof, provided at least 25% of the perimeter is constructed to ensure that ventilation is not impaired, e.g. meshed fencing.

Where there are enclosed or semi-enclosed storage areas which provide protection from the weather, they shall be constructed in such a way as to provide no opportunity for the build-up of gases in enclosed spaces. Low and high level natural ventilation is particularly important since many gases are heavier or lighter than air. Low level openings shall be above the height of any spillage retention sills. The store shall be designed and managed so that gas leaks cannot collect in confined spaces.

Open wire mesh of industrial quality, or steel louvers, are suitable materials for use as free venting sides.

Site Boundary and Security. Access to gas cylinder storage facilities shall be restricted to authorised personnel only. The storage site shall be secured by locked gates or doors appropriate to the location of the site. An industrial security fence, wall, or other impenetrable barrier shall surround the site to prevent trespassing, sabotage, vandalism and other forms of unauthorised access; such barriers are to be at least 1.8m high. A thermal radiation wall may be considered as part of the enclosure.

Storage Capacity, Access and Egress. Gas cylinder storage facilities shall be designed with adequate access and egress; and to allow unhindered cylinder movement. There shall be good access for delivery vehicles; and for the collection of gas cylinders on cylinder trolleys, etc. Manual handling is to be kept to a minimum, with consideration given to the use of powered mechanical handling aids. Design considerations include:

Segregation of vehicle and pedestrian exit and entry routes.

Well set out vehicle routes, avoiding sharp corners, blind bends and areas with low headroom and overhead power cables within the facility.

Use of the proper equipment, such as cradles or pallets, for lifting and transporting gas cylinders.

For safe access to cylinders and good stock control, aisles shall be provided and shall be a minimum of 1.0m wide.

Clear access for the emergency services shall be maintained at all times.

In areas where vehicles have access to, or are in close proximity to, the gas cylinder storage facility, protection shall be provided to prevent damage from vehicles. For example, this may be a low wall, bollards, or a crash barrier.

Adequate means of escape shall be provided. Access shall consist of one main entrance, with two doors, with one or more emergency exits provided for persons working in the area, with one door, on the opposite side to the main entrance. For smaller stores, access and egress can be via a single entrance, which can also be considered as the emergency exit. For larger stores, where the walking distance from any point within the store to any egress point is greater than 12 m, then additional emergency exits shall be provided. All emergency exits are to open in the direction of escape and are to be fitted with panic furniture of a type not requiring a key, card, or code to open. They are to provide an unobstructed means of escape and in operation are not to obstruct any other escape route. These exits shall be properly identified by signage, be unobstructed and maintained in a serviceable condition at all times

Gas Detection. Based on foreseeable hazards identified during the Risk Assessments (refer to Part 2, Chap 1), and where it is appropriate, atmospheric monitoring and/or alarm systems should be provided within the gas cylinder store to detect gas leakages.

Appropriate conditions include the storage of refrigerant and fluorinated gases (refer to Part 2, Chap 14); and gas cylinder stores, sited near Vulnerable Populations, that hold significant quantities of flammable and/or toxic gases. Advice may be sought from the Defence Fire & Rescue Service Fire Safety Officer.

Cylinder storage areas storing very toxic gas cylinders shall not be secured against building walls. For additional information refer to BCGA CoP 18 The Safe Storage, Handling and Use of Special Gases.

Telephone(s). A suitable telephone to aid emergency response shall be provided. It is to be within 50 m of the store. A land-line is the preferred option; however, for remote sites, a fixed cell-phone telephone may be provided. In all cases, a copy of the emergency response procedures and the contact details specified at the site entrance shall be provided adjacent to the telephone.

## Outdoor Gas Cylinder Storage Compounds - Signage

Safety signs and warning notices. Appropriate and legible warning signs and pictograms shall be displayed and maintained in good condition in accordance with the Chemicals (Hazard Information and Packaging for Supply) Regulations 2009 Chemicals (Hazard Information and Packaging for Supply; Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations Carriage of Dangerous Goods; and the Health and Safety (Safety Signs and Signals) Regulations 1996 Safety Signs and Signals. All signs shall be in English wording. For installations located overseas there is a legal obligation to provide notices in the language relevant to the local civilian population and work force (operator). However, bilingual / multilingual signs may also be necessary within sites based in the United Kingdom.

Boundary warning signs and pictograms shall be clearly visible from all angles of approach, preferably sited with the centre of the sign at the average eye level (between 1.5 and 1.7m above the ground). In exceptional cases, sites may be subject to the imposition of additional requirements by their local authority.

All gas storage sites shall display the following signs/pictograms/notices on the access point and boundary fence or wall:

Danger – explosive gases.

No smoking.

No naked flames.

No mobile phones.

No access to unauthorised personnel.

No storage of oil, grease or combustible materials.

Example Gas Storage Site Sign.

The same information may be displayed using other authorised signs, pictograms and notices. Refer to Annex A to this Chapter for example signs and pictograms. In addition, areas classified as Hazardous under DSEAR (see JSP 375, Part 2, Vol 1, Chapter 9) require an Explosive Atmosphere sign to be displayed at points of entry.

The appropriate diamond hazard labels shall also be displayed. However, if the stored gases would require more than two subsidiary diamond hazard labels, the primary diamond hazard label(s) should be used instead (refer to Part 2, Chap 3).

If acetylene cylinders are stored within the facility, then appropriate signs shall be displayed to alert the emergency services of their presence.

Example Acetylene Cylinder Sign.

At the entrance to the site the appropriate fire signs and notices (e.g. Fire Action Notice) are to be displayed. Refer to the example signage in par 51.”

A sign shall also be displayed detailing any specific action to be taken in the event of an incident/emergency and showing whom to contact in the event of an incident / emergency, with all appropriate contact details. This is to include the unit’s emergency contact details and the contact details for the gas supplier and the gas supplier’s 24-hour emergency contact telephone number (refer to Part 1, Chap 6). The location of any access keys, as well as the contact details for the authorised key holder shall be displayed.

## Outdoor Gas Cylinder Storage Compounds - Fire Safety

Gas Cylinder storage areas shall be located away from areas of fire risk. It is imperative that any area identified for storing gas cylinders is acceptable to the regional Defence Fire & Rescue Service Fire Safety Officer, who shall be involved in the planning and siting of the gas cylinder storage facility from the earliest stages, and who is to be consulted on all aspects of fire safety, including the types of cooling and extinguishing systems, and the number of First Aid Fire Appliances required for each gas cylinder storage facility. A Fire Safety Risk Assessment is to be carried out on all storage sites and is to be incorporated into the Site Fire Safety Management Plan.

Consideration shall be given to the use of automatic fire detection and alarm system, the requirement for fire hydrants, and a water spray system that will operate either automatically or manually.

A minimum of two fire extinguishers suitable for use on a Class C (gases or liquefiable gases) fire are recommended at all gas cylinder storage areas. For flammable gases such as LPG, it is recommended that these extinguishers should be 2 x 9 kg dry powder fire extinguishers. The appropriate number and type of fire extinguishers are to be provided and correctly located in accordance with the assessment made by the regional Defence Fire & Rescue Service Fire Safety Officer. Fire extinguishers shall be positioned in a readily accessible position close to each entrance/exit.

Additional safety equipment, such as positive pressure breathing apparatus, a water shower and eye wash bottle, may be required, dependant on the site risk assessment carried out by the competent person.

The site / establishment shall keep a record of the gas cylinder store(s) / compound(s) / facility(s) as part of the sites Hazards register. This record should include information on products stored, their maximum quantities, and their hazardous classification. This record shall be updated on a regular basis and be made readily available and accessible to the emergency services etc, in the event of an incident.

Segregation of combustible materials. To reduce the fire hazard to a minimum the area surrounding the cylinders is to be kept clear. Long grass, weeds and any overhanging branches are to be removed. A space of 3 m around the storage area is to be kept clear of all vegetation and combustible material. In addition, the undergrowth is to be kept as short as possible for a total distance of 9 m around the storage area. Chemicals such as sodium chlorate and other oxidising agents which may cause a risk of fire shall not be used as a weed killer.

No Smoking. Gas cylinder storage facilities shall be designated a “NO SMOKING AREA” and no smoking shall be permitted within a minimum distance of 3m of the storage facility boundary, (refer to Annex B to this Chapter).

## Outdoor Small Quantity Gas Cylinder Stores (e.g., Cages)

An external cylinder cage shall meet the requirements of this JSP as far as reasonably practicable and may be considered when:

1. Only small quantities of cylinders are stored, (maximum of 5 Cylinders).
2. Where the cylinders are required in support of the business activity within the parent building, particularly when they may be required outside of normal working hours.

Where there is not a permanent gas cylinder store on-site or where access to the on-site store is limited.

Siting. The location of the cage shall be subject to a Siting Board and a risk assessment (refer to Part 2, Chap 1). The assessment shall take account of any local hazards etc. e.g. emergency exits, machinery and ventilation inlet and outlets, closeness to offices, office windows, parking areas, walkways and shall ensure that there is plenty of natural ventilation around the site. The assessment shall also ensure that access to the cage is acceptable, both for personnel and for the delivery / collection of gas cylinders. The minimum safety distances at Annex B to this Chapter shall be observed.

Construction and Layout. The cage shall be secured against a solid wall. The wall shall have a minimum fire resistance of 60 minutes and a minimum height of 2m. The cage shall be secured onto a raised concrete base capable of taking the gross weight of the cage and its contents and able to minimise the amount of contact with cylinders from ground water. To aid mechanical handling a ramp may need to be provided. Consideration is to be given to the installation of protective barriers around the store to prevent direct contact, for example, from passing vehicles.

A fully enclosed cylinder cage. It is to be constructed using open mesh panels. The mesh is to be of such a size as to prevent tampering with the cylinders and valves. A sturdy and fully welded construction with high impact resistance. Minimum finish standard is a zinc finish, galvanised to BS EN ISO 1461. Wall and floor anchor points shall be provided for fixing down. Access doors shall be fully lockable, and of sufficient width to allow the movement of authorised personnel, cylinders and any mechanical handling aids required. If required, provide protection from the elements by the use of a fire-resistant, covered sloping roof. Appropriate safety signs and warning notices shall be fitted (refer to Annex A). Consideration is to be given to the safety of personnel accessing the store outside normal working hours.

Organisation. The range of cylinders stored shall be limited to those required for a particular application e.g., medical gas cylinders or welding gas cylinders.

The cage may contain both cylinders in use (e.g., connected to a manifold, as well as cylinders in storage.

The cage may be used to store portable gas sets or trollies complete with cylinders.

## Gas Cylinder Storage inside Specially Constructed Buildings - Siting

Gas cylinder storage places within buildings are not recommended and shall not be considered for new sites.

The justification for the chosen type of indoor gas storage room shall be recorded by the competent person.

If there are no alternatives to the indoor storage of gas cylinders, the storage area shall be on the ground floor of a building and follow a justification hierarchy, in order of preference as follows:

The store shall be a bespoke standalone designed and dedicated for the sole purpose of gas cylinder storage, be a adequately naturally ventilated building with appropriate segregation.

The store shall be in a dedicated room, sealed from the rest of the building, with adequate natural ventilation from the outside. The store shall only be assessable from an external door.

The store shall be in a dedicated room, sealed from the rest of the building, with suitable and sufficient forced air ventilation. The store shall only be assessable from an external door.

The store shall be in a dedicated room, adjacent to an outside wall, inside a building, with adequate natural ventilation to the outside. The store shall be sealed from other areas of normal occupancy.

The store shall be in a dedicated room, inside a building, with suitable and sufficient forced air ventilation. The store shall be sealed from other areas of normal occupancy.

The indoor storage room / compartment (irrespective of type listed above), shall be subject to a risk assessment (refer to Part 2, Chap 1) that shall consider as a minimum (but not be limited to):-

Properties of the gases.

Density of gas.

Risk of explosion from flammable gas release.

Quantities of gas cylinders stored.

The location of store in relation to other parts of the building.

Fire impacting on the cylinder store.

Leakage from valves or safety relief devices.

Ventilation requirements.

Access and egress from cylinder store.

Detection equipment.

Exposure of personnel to compressed gases.

## Gas Cylinder Storage inside Specially Constructed Buildings- Construction and Layout

Ventilation. Buildings containing the gas cylinders are to be adequately ventilated to prevent the accumulation of explosive or dangerous concentrations of gas. The rules for ventilation of buildings containing gas cylinders or cryogenic fluids are the same as those prescribed for explosive storehouses (refer to DSA 03 - OME Part 2 - Defence Code of Practice ).

Humid storage conditions are unsuitable for the storage of gas cylinders. In humid regions, mechanical ventilation systems may be necessary.

The store shall have thorough ventilation; a minimum of 12 air changes per hour is recommended. Ventilation openings shall be carefully sited in accordance with Annex B to this Chapter.

Buildings containing flammable gases shall have openings of not less than 2.5 % of the combined area of the walls and roof of the room or 12 % of the area of one of the external walls, whichever is the greater. Ventilation openings shall not normally be provided in internal walls.

If a forced ventilation system is used, it shall be connected to an alarm system to warn of failure.

Gas detection. Atmospheric monitoring shall be provided within the store to detect gas leakages. Foreseeable hazards will have been identified during Risk assessments (refer to Part 2, Chap 1), e.g. leakage of oxidising, asphyxiating, flammable gases, F-gases and/or fire. Based on the risk assessments, suitable gas detectors shall be fitted to warn of any hazardous atmospheres within the store. Alarm warnings, e.g. flashing lights, alarms, etc, shall be provided both outside and inside of the store (refer to Part 1, Chap 6).

Electrical equipment. All electrical equipment shall be selected, installed, and maintained dependent upon the findings of the DSEAR Risk assessment. If “explosive protection” equipment is required, it is to be provided to the approved classification / specifications (refer to BS EN 60079-10, BS EN 60079-14) and maintained accordingly (refer to BS EN 60079-18).

Gas Cylinder Handling. Consideration needs to be given to the use of powered mechanical handling aids such as forklift trucks within the confined space of an internal store.

Safety Management. Consideration needs to be given to the properties of the gases being stored and the building features which will allow leaks, spillages, fires, etc. to be managed safely.

Gas cylinders shall not be stored adjacent to radiators or other sources of heat, nor is electric apparatus to be operated in the vicinity of storage buildings containing gases (refer to Annex B to this Chapter).

Cylinders of very toxic or pyrophoric gases shall not be stored in internal stores.

The number of gas cylinders shall be kept to a minimum.

## Gas Cylinder Storage inside Specially Constructed Buildings - Signage

Signage. The building shall be suitably labelled (refer to Annex A of this Chapter) on the outside to assist firefighting and security operations in identifying the risks inside the building.

## Gas Cylinder Storage inside Specially Constructed Buildings – Fire Safety

Fire and explosion mitigation. The store shall be constructed of non-combustible materials. Where it forms part of a larger building, it shall be separated from the rest of the building by a firewall constructed of material rated to provide at least 60 minutes fire resistance. Brick and concrete are the preferred materials for firewalls.

The store shall have an area equal to at least one wall, or the roof, made of open mesh or lightweight friable material to provide explosion relief. This relief partition should be designed and positioned so that any explosion would vent safely without producing dangerous projectiles.

## Indoor Small Quantity Gas Cylinder Stores (e.g. Cabinets)

Siting. Any gas cylinders or cartridges stored internally shall be kept to the minimum necessary. Limited quantities of gas cylinders / cartridges may be stored inside a building within a dedicated cabinet(s). Each cabinet may store up to a maximum volume of 220 litres of gas. A maximum quantity of 400 kg of LPG cylinders / cartridges may be stored inside a building. The building and all cabinets located inside that building shall meet the following requirements.

Construction and Layout - Building. The building shall be of single-story construction and shall not house vulnerable populations.

The use of this area of the building for the storage of gas cylinders shall be included in the building safety plans. An appropriate Fire Safety Risk Assessment of the site shall be carried out and shall be incorporated into the site Fire safety Management Plan.

Construction and Layout - Building – Cabinet. The cabinet shall be located either at or above ground level. It shall not be located where it could prejudice any escape route.

The cabinet shall comply with BS EN 14470-2. It shall be constructed of non-combustible materials. It shall provide a minimum of 60 minutes fire-resistance. It shall be secured in position and have a lockable door which shall be kept locked when not in use.

If it has an internal volume greater than 0.5 m3, it shall be fitted with explosion relief equal to at least half the area of the back or side of the unit which discharges to a safe place outside the building

Ventilation. It shall be ventilated at high and low levels to a safe place outside the building.

Signage. All relevant safety signs and warning notices detailed in Annex A to this Chapter shall be displayed, including the emergency actions and contact details.

Fire Safety. Appropriate controls shall be enforced to minimise any hazard within the room or within adjoining rooms, with an assessment of the use of electrical equipment, naked lights and a ‘No Smoking’ policy. The area around the cabinet shall be kept free of combustible materials. Refer to Annex A & B to this Chapter.

## Bibliography
Regulation EU No 517/2014: REGULATION (EU) No 517/2014 OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL of 16 April 2014 on fluorinated greenhouse gases and repealing Regulation (EC) No 842/2006

Carriage of Dangerous Goods and Use of Transportable Pressure Equipment: The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations 2009

Chemicals (Hazard Information and Supply): Chemicals (Hazard Information and Packaging for Supply) Regulations, 2009.

DSEAR: HSE L138 Dangerous Substances and Explosive Atmospheres, Dangerous Substances and Explosive Atmospheres Regulations 2002. Approved Code of Practice and Guidance.

COSHH: UK Statutory Instruments2002 No. 2677, The Control of Substances Hazardous to Health Regulations (COSHH) 2002.

DSEAR: UK Statutory Instruments2002 No. 2776, The Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) 2002.

The Equipment and Protective Systems Intended for use in Potentially Explosive Atmospheres Regulations: UK Statutory Instruments2016 No. 1107, The Equipment and Protective Systems Intended for Use in Potentially Explosive Atmospheres Regulations 2016.

ADR: United Nations, Economic Commission for Europe Committee on Inland Transport. European Agreement Concerning the International Carriage of Dangerous Goods by Road. (ADR).

Safety Signs and Signals Regulations: UK Statutory Instruments1996 No. 341, The Health and Safety (Safety Signs and Signals) Regulations 1996.

Management of Health and Safety at Work Regulations: UK Statutory Instruments1999 No. 3242, The Management of Health and Safety at Work Regulations.

RIDDOR: UK Statutory Instruments2013 No. 1471, The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations (RIDDOR)2013.

BCGA COP 44, The Storage of gas Cylinders.

BCGA CoP 18 The Safe Storage, Handling and Use of Special Gases.

BCGA Code of Practice 35 - Filling Ratios and Developed Pressures for Liquefied and Compressed Gases.

LPG Industry Codes of Practice No. 7 “Storage of Full and Empty LPG Cylinders and Cartridges.

BS EN 14470-2, Fire safety storage cabinets for pressurised gas cylinders.

BS EN 60079-10-1, Explosive atmospheres. Classification of areas. Explosive gas atmospheres.

BS EN 62305-1 Protection against lightning. General principles.

BS EN 60079-14 - Explosive atmospheres. Electrical installations design, selection and erection.

BS EN 60529:1992+A2:2013 - Degrees of protection provided by enclosures (IP Code)

BS 5266-1:2016 - Emergency lighting. Code of practice for the emergency lighting of premises.

BS EN ISO 7010:2020+A1:2020 Graphical symbols. Safety colours and safety signs. Registered safety signs

BS 5499 - Graphical Symbols and Signs. Safety Signs, Including Fire Safety Signs.

BS 7430:2011+A1:2015 Code of practice for protective earthing of electrical installations.

JSP 317: JSP 317 - Joint Service Safety Policy for the storage and handling of Fuels, Lubricants and Associated products.

JSP 375: JSP 375: Management of Health and Safety in Defence.

JSP 392: JSP 392: Management of Radiation Protection in Defence.

JSP 418: JSP 418: Management of Environmental Protection in Defence.

DSA 03 OME REGULATORY DOCUMENT SET.

Movements and Transport Policy: JSP 800 - Defence Movements and Transport Policy

DBR 1754: DBR 1754 – Regulations for the Safe Storage and Handling of Petroleum Products in HM Ships and Submarines.

Medical gases Health Technical Memorandum 02-01: Medical gas pipeline systems, Part A: Design, installation, validation and verification

# Annex A - Industrial Gas Cylinder Storage Facility Signage

Table 9.A.1 - Gas Stores / Compounds Generic Signage
No unauthorised access	No source of ignition	No smoking	No mobile phones
#### Danger / Gas Cylinder Store		#### Danger / Forklift vehicles operate in this area	Warning Flammable / Gas
Gas Compound / Storage Facility	Potential asphyxiating atmosphere	Presence of Industrial vehicles	Flammable Gas
Acetylene	Warning / Oxidising Gas	Warning / Corrosive Gas	Danger / Explosive atmosphere
Acetylene	Oxidant	Corrosive Gas	Explosive Atmosphere
			Warning / Toxic Gas
Safety boots must be worn	Eye protection must be worn	Safety gloves must be worn	Danger of toxic gas

Table 9.A.2 - Examples Combination Signs
Inert Gas Store
Flammable Gas Store / Note: If Acetylene is stored then “Acetylene” signage should be used
LPG Gas Store

Table 9.A.3 - Examples of Signage for the Inside of an Industrial Gas Cylinder Store (Gas types / hazards as required)
KEEP CYLINDERS / UPRIGHT AND SECURE	Toxic / Gas
Flammable Gas	Corrosive / Gas
Inert / Gas	Oxidant / Gas

# Annex B - Minimum Recommended Safety Separation Distances for Industrial Gas Cylinders
Table 9.B.1 - Minimum Separation Distance (m) from Industrial Gas Cylinder Store[5] Boundary to Other Activities
[5] The separation distance is measured from the boundary of each store, or for individual cylinder packages, their outer edge, where they are not located in a store.
Ser	Type of Exposure	Inert	Flammable	Oxidiser	Toxic / Corrosive	Comments
1	Smoking, naked flames, sources of ignition and heat sources;	1	3	1	3	LPG cyls / <400 kg =1m / >400 kg = 3m / (Notes 1-3)
2	Combustible materials, e.g. paper, wood.	0	3	3	3	(Note 4)
3	Wooden structures buildings	0	3	3	3
4	Air compressors and ventilator intakes	3	3	3	3	Store shall not be directly below an air intake. Lighter than air gases may require specific RA.
5	Air compressors and ventilator exhausts	1	3	3	3	Exhaust heat / air quality. Potential harmful effects on gas cylinders
6	Openings / windows; building escape routes	1	2	1	3	For wooden structures use (serial 3)
7	Assemble areas (parade ground, muster points)	1	3	1	3	As long as store is not seat of fire!
8	Vehicle car parks	0	3	1	3	Store has adequate protection against vehicle impact
9	Pits, ducts, surface water drain. Openings below ground level	0	2	0	0	Liquids / heavier than air can accumulate below ground level
10	Fuel gas vent pipes	0	3	3	3
11	Machinery / process equipment	0	3	3	3	Document / / Risk Assessment. ATEX / DSEAR Compliance? Note 6
12	Unprotected Electrical Equipment	1	3	1	1	Document / Risk Assessment. ATEX / DSEAR Compliance? Note 6
13	Site boundary- where store boundary is site boundary	1	3	1	3	The distances stated are from the cylinder to boundary fence. (Notes 1-3)
14	Vulnerable populations (med centres, crèches)	8	8	8	8
15	Cryogenic storage tanks	1	inert cyro= 1 / oxidant cyro<2000L / =5 / oxidant cyro>2000L / =8	1	1	(Note 5)
16	Flammable liquid tanks <1000L	3	3	3	3
17	Bowman radios	0	HF radios 70 / VHF 15 / UHF 15	3	3	(Note 7)
18	Roadways (other than those required for access)	Requires specific RA. Gas cylinders shall not be stored underneath road bridges, archways.
19	Medium Voltage / High Voltage substations	Requires specific RA.
Notes: / Refers to LPG of between 50 – 1,000 kg; not required for less than 50 kg LPG. Cylinders of LPG with a total stored capacity less than 50 kg may be stored with other gas cylinders. / Cylinders of LPG with a total stored capacity greater than 50 kg but less than 1000 kg shall be segregated from other gas cylinders within the industrial gas cylinder compound, but the separation distances in this table shall take precedent. / For cylinders of LPG with a total stored capacity greater than 1,000 kg a separate store shall be provided, and the LPG cylinder compound separation distances shall take precedent. See Annexes below. / A minimum separation distance of 3m from the perimeter of the gas cylinder storage area shall be free of long grass, weeds, and overhanging branches. / Bulk storage is defined as static vessels of capacity greater than 1,000 litres, into which the produced is delivered. For bulk storage between 1,000 litres and 200 tonnes capacity, the separation distance shall be increased to 8 m from flammable gases and LPG cylinders above 50 kg total capacity. / A risk assessment may identify a need for protected electrical equipment or may justify a change to the separation distance for un-protected electrical equipment. / All Bowman transmissions (except Personal Role Radio (PRR)) are to be disabled in the vicinity of flammable gases within the safety distances detailed below (this includes gas cylinder stores as well as liquid oxygen storage and operational sites).

            1. Refer to HSG 176 for Minimum Separation Distance (m) from Industrial Gas Cylinder Store Boundary to Other Classes of Packed Dangerous Substances.
            2. Where Dangerous Goods are stored in bulk, close to a gas store an additional risk assessment shall be carried out to determine the minimum recommended separations distances, as they may be greater than those for packed Dangerous Goods. Refer to JSP 317 - Joint Service Safety Policy for the storage and handling of Fuels, Lubricants and Associated products JSP 317.

# Annex C - Design and Layout for Industrial Gas Cylinder Storage Areas - Examples
            1. This Annex is intended to provide guidance on best practice for the design and layout of storage areas for compressed and liquefied industrial gases. The layouts have been chosen to illustrate the factors that must be taken into account to achieve good stock management and effective access. These include:

Gas cylinders segregated according to product - hazard type.

Full and empty gas cylinders stored separately.

Where medical gas cylinders are held, they shall be stored in separate stores. If unavoidable they shall be segregated from non-	medical gas cylinders[6].
[6] Medical gases are classed as medicines and fall within MHRA – not HSE jurisdiction.

Walkways of sufficient width to enable handling of gas cylinders.

Adequate access for emergency use.

Provision for cylinders to be properly secured in an upright position.

Provision of fire-fighting equipment.

Appropriate signage.

These layouts are not intended to be used as the definitive solutions to the design and layout of all sites. They are reproduced to provide guidance. All new and refurbished sites are to be subjected to a Siting Board. All gas cylinder storage facilities shall be assessed for compliance with this publication.

If small quantities[7] of LPG cylinder are stored in industrial gas cylinder compounds, then the guidance in Annexes A, B and C to this Chapter shall take precedence. If LPG cylinders are stored in LPG only gas cylinder compounds, then the guidance in Chap 18 Annexes A, B and C shall take precedence.
[7] Quantities as stated in Annex A to this Chapter.

Notes: / Fencing shall be steel mesh construction. / Appropriate warning signs shall be displayed. / Where medical gas cylinders are held, they shall be segregated from non-medical gas cylinders. / A minimum of two fire extinguishers are to be provided at all gas cylinder storage areas. / Separation distance based on gas classification of cylinders designed to be held in the store[8] (refer to Table 9.B.1). / If the gas compound perimeter fence serves as the site / establishment perimeter fence; then the values stated in Table 9.B.1 shall be used as the separation distance between the cylinder and the site boundary.
[8] Separation distance based on store design and theoretical holdings, not daily holdings.

Figure 9.C.1: Example 1: Layout of a Typical Industrial Gas Cylinder Storage Compound[9].
[9] Industry bodies representing “industrial gases” and “LPG” are British Compressed Gas Association – BCGA and Liquid Gas UK. Both industry bodies apply separation distances for gas cylinder storage by using different risk models.

Notes: / Separation distance from Table 9.B.1. / Height of firewall shall be 2m minimum - refer to paragraph 29.

Figure 9.C.2: Example of Separation Distance using a Firewall

# 10 - Organisations and Management of Gas Cylinder Storage Compounds

Sponsor - DSFA Technical Gases Manager

## Scope

      1. This Chapter provides guidance on roles and responsibilities of Gas Cylinder Compound Managers and how they safely store and manage gas cylinders within the different types of gas cylinders compounds described in Part 2, Chap 9.

## Gas Cylinder Grouping / Segregation / Identification

            1. Gas cylinders shall be grouped within the store according to a formal plan. This plan is to take into account the hazards posed by the gases stored; the types of gas cylinders; handling techniques; and the general requirements of good storekeeping.

            1. Gas cylinders of the same gas or the same hazard category shall be grouped together, e.g. flammable, toxic, oxidising, or corrosive (refer to Part 2, Chap 3).

            1. Medical gas cylinders should be stored in a separate gas store whenever possible. Medical Gas Cylinder Stores shall comply with the Medicines Healthcare Regulatory Authority (MHRA) Codes of Practice. Pathology gases are not classified as medical gases and are to be segregated from medical gases.

            1. LPG cylinders are to be stored according to the total capacity as shown in the table below:

Total Capacity	Storage	Remarks
Less than 50 kg	LPG cylinders may be stored with other gas cylinders of the same hazard category	Refer to Para 3 above
Between 50 kg to 1,000 kg	LPG cylinders shall be segregated within the store from other gas cylinders	Refer to Part 2, Chap 9 Annex B

            1. Full and used gas cylinders shall be segregated.

            1. Unserviceable gas cylinders are to be further segregated and separated from serviceable cylinders.

            1. Areas within the gas cylinders storage facility shall be clearly identified by signage to show the condition, ownership and contents of gas cylinders.

## Cylinder Orientation and Security

            1. Gas cylinders shall be stored in accordance with the supplier’s guidance and maximum use should be made of specially designed pallets.

            1. Gas cylinder pallets are available from the current MOD gas supply contractor, which is managed by Team LEIDOS.

            1. Unless the gas supplier provides contrary guidance, all gas cylinders shall be stored vertically. This can be in cradles, pallets, trolleys or other specifically designed stowages.

            1. Gas cylinders stored in a vertical position shall be stored no more than one cylinder high. However, smaller gas cylinders may be stored more than cylinder high when stored in purpose designed pallets, in accordance with the gas supplier’s approval.

            1. All gas cylinders shall be securely restrained to prevent them from falling over. Gas cylinders, which are stored in a gas cylinder trolley, shall be secured to an appropriate strong point to prevent the combined trolley and gas cylinder falling over. Securing gas cylinders within the gas suppliers designed pallet is an acceptable method of restraint within the gas store.

            1. Certain compressed gases are supplied in gas cylinders with rounded bottoms. Where these are stored vertically, special stowages specifically designed to accommodate round-bottom cylinders shall be used.

            1. Where gas cylinders are stored horizontally, special arrangements shall be required to secure them. They shall be suitably restrained on dunnage. Horizontally stored gas cylinders are not to rest directly on the floor. Particular care is to be taken to prevent the onset of external corrosion (e.g. by ensuring gas cylinders do not rest in pools of water).

Note: Horizontal gas cylinder storage can allow any water, or other contaminants, inside the gas cylinder to corrode the wall along the parallel section where it is thinnest and most highly stressed.

Storage of Goods within a Storage Compound. The only items to be stored in a gas cylinder storage compound are gas cylinders; their associated fittings, such as cylinder keys, valve caps, etc; and associated mechanical handling aids, such as cylinder trolleys. Combustible stores of any description, e.g., oils, greases, paints, fuels; other classes of Dangerous Goods; salt or corrosive chemicals shall not be stored in the same storage compound / building as gas cylinders. The storage compound shall not be used as a lay-apart store or as a convenient storage area for other items.

Stock Rotation. Gas cylinders are not to be stored for excessive periods of time. Only demand sufficient quantities of gas to cover actual unit requirements. Stock rotation should be practised in line with normal stock control procedures, i.e., to ensure that wherever possible first-in is first-used. This is particularly important when the gas cylinders are exposed to the elements. Certain gases are lifed; and that all gas cylinders are subject to periodic inspection and test requirements.

Cylinder Rental Charge. Cylinders are provided on a rental arrangement with the supplier and incur a monthly rental charge for each cylinder a unit hold, cylinders that are no longer required or are empty are to be returned to the supplier at the earliest opportunity.

Gas cylinders containing a gas that is time expired shall be returned to the supplier. Gas cylinders past their periodic inspection and test date may be issued for use within the unit / confines of the establishment, (provided the contents are in-life), but the gas cylinder must not be refilled (refer to Part 2, Chap 5), or be transported on the public highway (refer to Part 2, Chap 8). It is recommended that all gas cylinders which are past their periodic inspection and test date are returned to the supplier and as required, replaced with serviceable items.

Units must check the gas life (if applicable) and periodic inspection and test life of all cylinders at receipt. Gas cylinders that fail to meet the minimum requirements blow are to be rejected and returned to the supplier.

Gas cylinders are to be supplied with a minimum mechanical life remaining before its next periodic inspection and test of at least 6 months;

Where gas cylinders are delivered for onward transportation, such as overseas, the minimum mechanical life is to be 1 year.

If a gas has a life allocated, it must be supplied with a minimum gas life of 1 year.

Leak Procedures. All units are to have written Standard Operating Procedures (SOPs) for managing leaking gas cylinders. These SOPs are to be available for all personnel working on the site. Any leaking gas cylinders are to be made safe and returned as unserviceable.

## Gases

Corrosive Gases. Gas cylinders containing corrosive gases shall be returned promptly to the supplier by the expiry date; and these gas cylinders may be subject to audits by the supplier (refer to Part 2, Chap 1).

Very Toxic and Toxic Gases. In all cases, full, in use or nominally empty gas cylinders of very toxic gases shall be kept in a suitably ventilated, locked enclosure. Access shall be restricted to trained and authorised personnel only. Please refer to BCGA CoP 18 The Safe Storage, Handling and Use of Special Gases for details.

Gas cylinders containing toxic gases are supplied with a valve outlet sealing plug or cap-nut which acts as a secondary seal. Slight leakage or the inadvertent opening of the valve can be hazardous if these seals are incorrectly fitted. Potentially, this hazard can also exist when gas cylinders are nominally empty. Whenever practicable, toxic gases are to be stored separately. Full and unhindered access to gas cylinders containing toxic gases will assist their routine checks and reduce the risk of accidental exposure should an incident occur.

Pyrophoric Gases. Pyrophoric gases are gases that spontaneously catch fire in air. Escaping gas cannot be extinguished; and extinguished gases may reignite spontaneously / explosively.

In all cases, full and nominally empty gas cylinders of pyrophoric gases shall only be stored in suitably, ventilated, and locked external gas cylinder stores. They shall not be stored within a building.

Access to gas stores containing pyrophoric gases shall be restricted to trained and authorised personnel only. Cylinders shall be protected from heat and other ignition sources, e.g. flames, sparks, etc, to prevent explosion.

Fluorinated Greenhouse Gases (F-gases) and Ozone Depleting Substances. Fluorinated Greenhouse Gases (F-gases) and Ozone Depleting Substances are subject to regulation. Regulation includes: the containment, use, responsible supply, recovery, disposal, destruction and labelling of both the gases themselves and products and equipment containing these gases (refer to Part 2 Chap 14 and JSP 418, Vol 2, Leaflets 6 & 7).

Units holding F-gas cylinders in stores are required to keep records, prevent leakages and to promptly repair any detected leakages. Record keeping shall include:

  1. The quantity of Ozone Depleting Substances and F-gases held.

  1. Quantities recovered from maintenance and service activities.

  1. Quantities disposed of or returned.

  1. Details of leakages, including quantity (refer to Part 2, Chap14).

All units holding these gas cylinders are to have written standard operating procedures for the storage of these gases and instructions to deal with leaking gas cylinders. Any leaking gas cylinders shall be promptly identified. If the leak cannot be contained then, if safe to do so, the contents of the leaking gas cylinder are to be transferred into a recovery cylinder and gas losses shall be reported.

## Considerations of High or Low Temperature Storage

Gas cylinders exposed to high levels of radiant heat have the potential to explode due to an increase in pressure. To prevent explosion under normal conditions, the gas cylinder supplier is required to carefully control the gas cylinder’s charge, in accordance with BCGA CP 35, to ensure that excessive pressure cannot develop under the highest ambient temperature range in the climactic area of use. Gas cylinders shall not be deliberately heated or knowingly stored where they are likely to become excessively heated.

Aluminium gas cylinders that are subjected to temperatures above 150°C will soften permanently and present a potential hazard even after the heat source has been removed.

Some steel gas cylinders, and their fittings may become brittle when subjected to temperatures below –20°C.

WARNING. Cold-soaked gas cylinders are to be handled with care. Avoid subjecting the gas cylinders to any impact or sudden shock.

Storage at low temperatures may affect the homogeneity of certain gas mixtures and this may inhibit the immediate bringing into service of a limited number of gas mixtures. For example, the medical gas mixture Entonox™ will separate out at temperatures below -6°C and will require conditioning before use (see Entonox™ Safety Data Sheet) Entonox; and calibration gas mixtures will need to be conditioned at room temperature before use.

LPG cylinders, especially butane cylinders, may not be useable at low temperatures due to lack of developed pressure (refer to Part 2, Chap 18).

Whenever a gas cylinder’s normal operating temperature limits are exceeded it is to be made safe and separated from serviceable stock. The gas supplier, or the Support Authority responsible for the gas cylinder, is to be informed and advice sought. If deemed unserviceable the gas cylinder is to be returned as unserviceable (gas cylinders subjected to excessive heat) detailing the reason for the unserviceability.

## Other Storage Considerations

Gas Cylinder Maintenance. No gas cylinder maintenance should be necessary in-service. If military units identify a requirement for maintenance, they are to declare the gas cylinder unserviceable and:

  1. Separate the gas cylinder from serviceable stock.

  1. Return the gas cylinder in accordance with Defence Logistic Framework (DLF).

Maintenance activities are only to be carried out by authorised, competent personnel.

Movement within the Facility. For housekeeping and stock control purposes, aisles shall be provided in storage areas to enable access to groups of gas cylinders. Typically, aisles should not be less than 1.0m wide and shall, in all cases, provide sufficient manoeuvring space for the types of mechanical handling equipment used at that site (refer to Annex B of Chapter 9).

The storage area shall be maintained in a condition that affords the unhindered safe movement of gas cylinders by trolley, forklift truck, etc, and to prevent damage to cylinders during manual handling, as well as trolleys, fork lift truck and other vehicular use. Clear access for the emergency services is to be maintained at all times. Store gas cylinders where they are not vulnerable to hazards caused by impact, e.g. from vehicles such as fork-lift trucks.

Material Handling Equipment. Power operated vehicles, MHE, and cranes can present a risk of fire and explosion when operating where flammable gas cylinders are stored. Under the provisions of the Dangerous Substances and Explosive Atmospheres Regulations 2002 (DSEAR) DSEAR , it is the responsibility of operators, with advice from TLBs to identify and risk assess the hazardous zones where MHE will operate, including operational theatres. Tri-Service Material Service Contracts Branch are responsible for ensuring that suitable, intrinsically safe MHE, based on operator risk assessments, is available and the Service Provider must to ensure that appropriate, intrinsically safe and serviceable MHE is supplied to the operator. Guidance for MHE regulation and training can be found at JSP_800 Vol_5, Part 2, Group 2, and section 2 - Leaflet 29.

Advice / guidance for the operation & use of the Tri-Service Material Handling Service PFI Contract can be obtained from:

TSMHS CMT
SVPT GSG
MOD Abbey Wood
Neighbourhood 5
Juniper 0, Wing 2
Mil Tel: 9352 39017
Civ Tel: 0117 91 39017

Small Quantity Stores. A suitably ventilated, marked and labelled, lockable cabinet may provide effective security for small quantities of gas cylinders / receptacles (refer to Part 2, Chap 9).

Fire extinguishers. Where fire extinguishers are stored in a gas store they are to be segregated from all other gas cylinders. Specifically, powder fire extinguishers are not to be stored with other gas cylinders. There is the potential for certain powders within these extinguishers to form a corrosive mixture when mixed with water which could affect the integrity of gas cylinders.

## Management of Gas Cylinders Storage Compounds

Gas cylinder store manager. A single person shall be appointed as the gas cylinder store manager. The manager must have the minimum competencies (for training refer to Part 1 Chap 4 to carry out the duties as detailed in this chapter.

The gas cylinder store manager shall ensure that the receipt, storage and issue of gas cylinders are carried out in accordance with all external and internal regulations, such as JSP 319. Ensure that operating procedures for the activities undertaken are drafted and disseminated appropriately. The list below provides, as a generic guide, the minimum responsibilities of the gas cylinder stores manager:

  1. The security of the gas cylinder store and the safe keeping of the gas cylinders within. Ensuring there is management control of the access keys to each gas cylinder store and that there is an up-to-date list of authorised persons who may draw those access keys.

  1. Providing a focal point for the store and ensuring compliance with all external and internal rules and regulations.

  1. Ensure that risk assessments for the activities undertaken are drafted that identify the hazards and risks within the gas cylinder store and that appropriate control measures are implemented to control the risks.

  1. Ensure that emergency procedures and plans are drafted and disseminated appropriately

  1. Liaison with the unit emergency response organisation, as appropriate, to provide access to the gas cylinder store by the Emergency Services during any incident.

  1. Accounting for all gas cylinders in the designated manner; and ensuring that receipt and issue checks are carried out.

  1. Ensuring that the weekly gas cylinder store inspection is carried out.

  1. Liaise with the Maintenance Management Organisation (MMO) and other contractors to ensure upkeep of the infrastructure; and compliance with the rules and regulations concerning safe working procedures, for example, within any confined spaces affected by the gas cylinder store.

  1. Where controlled gases are stored, e.g., F- Gases, maintaining a record of all holdings and any leakages.

  1. Where controlled gases are stored e.g. F-Gases, ensuring that the end–user has records demonstrating that personnel using F- Gas are competent to a nationally recognised qualification. The person-in-charge	of the “end user” department must ensure that all personnel within his command who use F-Gas are adequately trained to the respective national standard as mandated in EU Regulation 517/2014 EU Regulation 517/2014.

  1. Ensuring that only persons who are trained and competent to carry out their duties within the gas cylinder store are permitted access.

  1. When gas cylinders are moved from the holding unit to another unit, ensuring that Team LEIDOS Lubricants and Gases Manager are informed: information on the products, quantities and the relevant UINs is required.

Receipt and Issue Checks. Following all deliveries, and prior to all issues, checks shall be carried out to ensure all products are in a serviceable condition and the appropriate documentation is complete. All non-conformities shall be reported to the gas cylinder store manager. The checks are to include:

  1. The gas cylinder contents are correctly identified (refer to Part 2, Chap 3).

  1. The gas cylinder is in-date for its periodic inspection and test dates (refer to Part 2, Chap 3).

  1. A lifed gas is in-date for use (refer to Part 2, Chap 3).

  1. There is no obvious damage to the gas cylinder body.

  1. There is no obvious damage to the valve.

  1. Gas cylinder accessories, e.g., valve guard, protective cap, valve outlet protection, as appropriate are fitted, secure and serviceable.

  1. There is no gas leakage.

  1. Any certification necessary e.g., certificate of conformity, is provided (refer to Part 2, Chap 6).

  1. Safety Data Sheets are available for all products.

  1. All gas cylinders are accounted for in accordance with unit stores procedures.

  1. Unless required for use, all gas cylinders are kept in an authorised gas cylinder store.

Emergency Plans. A plan of the gas cylinder storage facility’s layout, identifying gas classifications, full and nominally empty gas cylinder locations, etc, especially the confirmed presence or confirmed absence of acetylene cylinders, will assist the emergency services when dealing with incidents in or around the storage site.

Example of Gas Cylinder Facility Layout Plan.

The gas cylinder store manager shall provide an appropriate emergency plan. This plan is to be made available to the emergency services via the unit Safety, Health, Environmental and Fire Officer as appropriate.

## Inspection of Gas Cylinders and Gas Cylinder Stores

The gas cylinders and their storage area shall be inspected by a competent person, at least weekly, under the authorisation of the gas cylinder store manager. All non-conformities are to be reported to the gas cylinder store manager. This inspection is to be recorded and records kept.

The inspection shall check for:

  1. There are no leaks.

  1. There is no obvious unserviceability.

  1. All gas cylinders are correctly grouped as appropriate.

  1. All gas cylinders are correctly orientated and are secure in their storage.

  1. All gas cylinders are within their periodic inspection and test life, and all lifed gases are within date for use (refer to Part 2, Chap 3).

  1. All gas cylinders are correctly marked and identified (refer to Part 2, Chap 3).

  1. Safety Data Sheets and any other certification (e.g., Certificates of Conformity) are available (refer to Part 2, Chap 6).

  1. There are sufficient gas cylinders to meet unit demands. All excess gas cylinders are to be returned.

  1. Empty, unserviceable or unwanted gas cylinders are returned at the earliest opportunity.

  1. The gas cylinder store is clean, with no obvious fire risks.

  1. Access and egress routes are clear.

  1. The gas cylinder store is secure.

  1. The gas cylinder store is not being used to store other items / dangerous goods.

## Bibliography

Carriage of Dangerous Goods and Use of Transportable Pressure Equipment: The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment Regulations 2009

Chemicals (Hazard Information and Supply): Chemicals (Hazard Information and Packaging for Supply) Regulations, 2009.

DSEAR: HSE L138 Dangerous Substances and Explosive Atmospheres, Dangerous Substances and Explosive Atmospheres Regulations 2002. Approved Code of Practice and Guidance.

COSHH: UK Statutory Instruments2002 No. 2677, The Control of Substances Hazardous to Health Regulations (COSHH) 2002.

DSEAR: UK Statutory Instruments2002 No. 2776, The Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) 2002.

The Equipment and Protective Systems Intended for use in Potentially Explosive Atmospheres Regulations: UK Statutory Instruments2016 No. 1107, The Equipment and Protective Systems Intended for Use in Potentially Explosive Atmospheres Regulations 2016.

ADR: United Nations, Economic Commission for Europe Committee on Inland Transport. European Agreement Concerning the International Carriage of Dangerous Goods by Road. (ADR).

Safety Signs and Signals Regulations: UK Statutory Instruments1996 No. 341, The Health and Safety (Safety Signs and Signals) Regulations 1996.

Management of Health and Safety at Work Regulations: UK Statutory Instruments1999 No. 3242, The Management of Health and Safety at Work Regulations.

RIDDOR: UK Statutory Instruments2013 No. 1471, The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations (RIDDOR)2013.

BCGA COP 44, The Storage of gas Cylinders.

BCGA CoP 18 The Safe Storage, Handling and Use of Special Gases.

BCGA Code of Practice 35 - Filling Ratios and Developed Pressures for Liquefied and Compressed Gases.

LPG Industry Codes of Practice No. 7 “Storage of Full and Empty LPG Cylinders and Cartridges.

BS EN 14470-2, Fire safety storage cabinets for pressurised gas cylinders.

BS EN 60079-10-1, Explosive atmospheres. Classification of areas. Explosive gas atmospheres.

BS EN 62305-1 Protection against lightning. General principles.

BS EN 60079-14 - Explosive atmospheres. Electrical installations design, selection and erection.

BS EN 60529:1992+A2:2013 - Degrees of protection provided by enclosures (IP Code)

BS 5266-1:2016 - Emergency lighting. Code of practice for the emergency lighting of premises.

BS EN ISO 7010:2020+A1:2020 Graphical symbols. Safety colours and safety signs. Registered safety signs

BS 5499 - Graphical Symbols and Signs. Safety Signs, Including Fire Safety Signs.

BS 7430:2011+A1:2015 Code of practice for protective earthing of electrical installations.

JSP 317: JSP 317 - Joint Service Safety Policy for the storage and handling of Fuels, Lubricants and Associated products.

JSP 375: JSP 375: Management of Health and Safety in Defence.

JSP 392: JSP 392: Management of Radiation Protection in Defence.

JSP 418: JSP 418: Management of Environmental Protection in Defence.

DSA 03 OME REGULATORY DOCUMENT SET.

Movements and Transport Policy: JSP 800 - Defence Movements and Transport Policy

DBR 1754: DBR 1754 – Regulations for the Safe Storage and Handling of Petroleum Products in HM Ships and Submarines.

Medical gases Health Technical Memorandum 02-01: Medical gas pipeline systems, Part A: Design, installation, validation and verification.

Confined Spaces Regulations 1997: UK Statutory Instruments1997 No. 1713, The Confined Spaces Regulations 1997.

BCGA CP44, THE STORAGE OF GAS CYLINDERS.

Regulation EU No 517/2014: REGULATION (EU) No 517/2014 OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL of 16 April 2014 on fluorinated greenhouse gases and repealing Regulation (EC) No 842/2006

# 11 - Organisation and Management of Bulk Cryogenic Liquid Storage Compounds

Chapter Sponsor - AC-PT GS1 & CGMS DECA Stafford

## Scope

            1. This Chapter provides guidance on roles and responsibilities of personnel operating in bulk cryogenic liquid storage compounds and how they safely store and mange cryogenic liquids within the compounds.

            1. In line with the general trend to move away from MOD-owned equipment towards Contractor-owned equipment, this chapter also considers the demarcation of responsibilities between MOD and the Contractor in respect of contractor-owned cryogenic storage vessels.

## Cryogenic Liquids, Health, Safety, Environmental and Security Arrangements

Main Hazards. The major hazards associated with the storage of cryogenic liquids are:

  1. Cryogenic spills resulting in cold injuries to personnel and cold embrittlement to equipment (refer to Part 2, Chap 12).

  1. Asphyxiation of personnel as the result of cryogenic liquid evaporating and the subsequent gas replacing atmosphere. (refer to Part 2, Chap 12).

  1. Oxygen enrichment increases fire risk as the result of liquid oxygen (LOx) evaporating and the subsequent gas replacing atmosphere.

  1. Gas properties post cryogenic liquid spill and subsequent evaporation. (Toxic, asphyxiant, oxidant, flammable, and ozone depleting substances) (refer to Part 2, Chap’s 1 and 12).

Risk Assessments. See Part 2 Chap 1 for generic gas systems risk assessments.

Plant Site Survey. All bulk cryogenic liquid storage compounds containing either MOD / Contractor owned bulk cryogenic storage vessels shall be subject to a Site Survey. The Site Survey shall be carried out by the appropriate Authorised Engineer (AE). The Site Survey is carried out in order to determine the Risk Categorisation of the plant and equipment on a particular Site or Establishment in accordance IAW JSP 375.

Leak Procedures. Before a site may be used for storing bulk cryogenic liquids, written SOPs for dealing with leaks and escapes shall be available for all personnel working on the site.

Training. The storage and handling of bulk cryogenic liquids shall be carried out only by appropriately trained personnel; and will normally require the provision of suitable handling equipment (refer to Part 1, Chap 5 - Training; and Part 2, Chap 7 – Handling and Use).

PPE. The appropriate PPE shall be worn when handling cryogenic liquids or entering a bulk cryogenic storage compound (refer to Part 2, Chap 2).

Ventilation. The provision of ample uncontaminated through-ventilation is essential to prevent the formation of undue concentrations of gases in the atmosphere of buildings housing cryogenic liquids. Temporary high concentrations may result from accidental spillage of the liquid, but these occurrences will themselves draw attention to the accompanying hazard. The creation of a dangerous atmosphere out of doors is unlikely except in the case of accidental discharge of the liquid in quantity.

Confined Spaces. Inspection pits, cable ducts, wells, or other Confined Spaces adjacent to an installation holding cryogenic liquids shall not be entered without a suitable and sufficient, written, Risk Assessment and/or Permit to Work, to assess whether the work can be done without the need for people to enter the confined space, identify the hazards present, assess the risks and determine what precautions are to be taken (refer to Annex A of this Chapter, the Confined Space Regulations and JSP 375, Part 2, Chap 28).

No person shall be permitted to enter any cryogenic liquid receiver, gasholder, or storage tank for the purpose of inspection or repair without a suitable and sufficient, written, Risk Assessment and/or Permit to Work (refer to the Confined Space Regulations Confined Space Regulations and JSP 375, Part 2 Chapter 28). All maintenance activates on cryogenic storage facilities shall be carried out in accordance with the relevant Safety Rule Books covering High Risk activities on Defence Infrastructure (JSP 375 Vol 3).

The discharge of cryogenic liquids shall always be directed out of doors to a safe point, such as a dedicated boil-off pit, and shall be prevented from entering drains, sewers, cable ducts, buried earthing plates/electrodes and bunded areas.

## Cryogenic Compounds-Siting

The following factors shall be observed when determining the site location of a bulk cryogenic liquid storage tank compound. They shall be included in the risk assessment for that site. For existing tank compounds that may not conform to these requirements a risk assessment shall be carried out, any risk shall be assessed and recorded, and appropriate safety procedures put in place until rectification action is taken. Refer to Part 1 Chap 6 for siting board requirements, further guidance can be found at JSP 850.

These factors specifically apply to the storage of liquid oxygen, however many of them have equal relevance to other cryogenic liquids.

  1. All breathing oxygen facilities shall have a constant source of fresh ‘uncontaminated’ ambient air. The necessary separation from threats to/from the site may well exceed the safety distances given in Table 11.1.

  1. Sites shall be located away from public roads and housing areas but shall provide easy access for gas suppliers and rescue vehicles. Where a cryogenic compound is sited close to a public road or traffic route, additional safety measures shall be carried out including:

The use of signs to warn passing traffic of the hazard within the storage area.

Including information about the storage area and the associated hazard in Unit induction briefing.

Providing information about the storage area and the associated hazard when issuing Unit driving licences and permits (e.g. Airfield Driving Permits).

Carry out local control of traffic, e.g. when carrying out replenishment or maintenance operations on tanks, when there is an increased risk of a spillage.

  1. Direct access to the aircraft parking platform area needs to be ensured.

  1. Consideration needs to be given to the main prevailing wind direction and the possibility of the movement of vapour clouds from cryogenic liquid spillages or venting; these are generally low-lying and may give rise to hazards such as poor visibility, oxygen-enrichment, oxygen-depletion, etc. The use of an indicator, such as a windsock or other device, to provide in the early stages of any spillage or discharge an indication of which neighbourhood might be exposed to plumes and/or plume ground strike is recommended.

  1. The location of the site shall be chosen so that damage by electrical arcing from overhead electrical or other cables cannot occur.

  1. Overhead Cables. Protection against lightning is not normally required. However, the risk should be evaluated and protection may be necessary to comply with local conditions or site regulations. Any necessary lightning protection should be installed in accordance with BS EN 62305-1 (Protection against lightning. General principles) and JSP 850 (Infrastructure and Estate Policy). The delivery organisation shall liaise with the DIO Construction Standards Manager.

  1. Underground Cables. Consideration shall also be given to the location of any underground cables and the effect that a major spillage may have on these cables.

  1. Electrical Bonding. Operating sites shall be fitted with electrical grounding straps to ground oxygen equipment for discharge of static electricity. Fixed bulk cryogenic storage shall also be bonded to earth.

  1. The site shall not be established in areas that could be exposed to flammable or combustible liquids or any kind of gases in the event of a piping rupture.

  1. Storage sites for liquid breathing oxygen shall neither be located on the top of structures, nor underground or in basements.

  1. Receptacles for liquid oxygen shall not be located in the vicinity of oil lines or areas in which hydrocarbons or other combustible materials can accumulate.

  1. If an oxygen storage area is established at a place which is located below an adjacent storage area for flammable or combustible liquids, appropriate measures, e.g. the construction of embankments, diversion dams, or steps, etc, shall be taken to prevent liquids from accumulating below the storage tanks.

  1. When operating aircraft in the vicinity, consideration needs to be given to the hazards associated with oil and grease contamination; fuel use and spillage; weapons systems; and the possibility of an ignition source from electrical equipment and radio/radar transmitters.

  1. Similar hazards shall be assessed from operating aviation Ground Support Equipment in the vicinity.

Further guidance on the location of bulk cryogenic liquid storage tanks is given, in respect of Safety Zones and Minimum Separation Distances, in in NATO Standard AAGSP-08 (STANAG 7175) and in BCGA Codes of Practice 26 and 36.

Safety distances, according to BCGA Codes of Practice 26 and 36 are based on experience and calculations of minor releases; not catastrophic failures. Table 11.1. provides a summary of some of the safety distances for LOx given in in NATO Standard AAGSP-08 (STANAG 7175) and/or BCGA Code of Practice 36 (the most conservative distance is given). LOx storage tanks and plant shall be located at a site which will minimise any risk to personnel, the local population, equipment and property. They shall not be close to areas where other hazardous materials are stored.

For all new installations a minimum safety distance of 1500 m from any areas of risk is to be applied.  If this is not practical, local protection around the site to prevent unauthorised access, any unwanted projectiles or contamination entering the area, whilst allowing thorough ventilation is necessary. A siting board for the installation would be expected to take this into consideration.

When assessing the risk from a cryogenic liquid or its vapour, the hazard produced may well exceed the safety distance determined from a fixed point. Liquid will travel until it settles at the lowest point and subsequently evaporates. Vapour clouds will be blown by the wind and, if in sufficient quantity, have the potential to travel far beyond the minimum safety distance quoted. This dynamic movement of cryogenic liquid and vapour is always to be taken into account when conducting siting boards for new / replacement facilities or when carrying out assessments of existing facilities.

Table 11.1 - Safety Distances from LOx storage tanks
Activity	Minimum Safety Distance (m)
Public road and railways	50
Flammable liquid / gases storage	25
Aircraft parking, refuelling & defueling	25
Parked vehicles	15
Traffic routes	15
Combustible solid materials	15
Any inlet to the public sewerage system	15
Buildings	15
Aircraft Taxiways	15
Asphalt surface	15
Meadow	15
Property boundary	15
Non-intrinsic mobile phones & other electrical devices fitted with batteries (see note)	15
Fire, open flame, light, smoking areas	15
Operation of Bowman radio: / HF Radios / VHF & UHF Radios	70 / 15
Note: This excludes approved solar-powered mobile phones permanently fitted to the bulk cryogenic storage, by the tank owner, to monitor the tank’s contents

## Cryogenic Compounds, Construction and Layout

Construction of storage areas. Existing MOD cryogenic storage tank areas are situated in a variety of locations, these include open compounds; buildings with open sides that are partially enclosed (Dutch Barns); or, totally enclosed (blast-proof shelters). Any new / replacement tanks are not to be situated in an enclosed storage area. New / replacement tanks are to be installed in accordance with the relevant BCGA Codes of Practice 26 and 36.

The floor material shall be concrete, and any surface treatment shall be non-oxidising and capable of withstanding the low temperatures resulting from cryogenic liquid spillages. Materials such as asphalt or other tar-based substances shall not be used.

The design of the flooring shall be more than sufficient to withstand the loading of full cryogenic storage tanks and any machinery or delivery tankers likely to be used for installation or charging. Consideration shall be given to the weight of additional equipment which may also be located on the plinth and the effects of volatile substances such as snow, ice etc. or loading from the wind.

The floor shall have a gradient (a slope of between 1:80 and 1:100 is recommended) sloping away from the storage tanks and the compound entrance. The design will allow spillages to be directed towards a non-hazardous area, a dedicated cryogenic liquid drainage channel, or a boil-off pit. Any containment walls around the plinth are not to allow the feet or external component parts of the tank to remain immersed in a cryogenic liquid.

Non-combustible partition walls or barriers are to be erected to prevent cryogenic liquid running off the site or entering storm drains, sewers, cable ducts, buried earthing rods/plates/electrodes, or bunded areas for other chemicals/products

Where horizontal tanks are installed under cover, winching points shall be provided behind each storage tank to allow the tanks to be drawn into position. There shall be no stops or uneven levels between the storage tank area and the outer apron to impede installation of the storage tanks.

Site Boundaries and Security. Physical security measures shall be established for cryogenic storage tanks and associated operating sites. These are to restrict entry to the site to authorised personnel who have had appropriate training and who understand the hazard within, and to prevent access to unauthorised persons.

In military areas, hazardous goods storage areas are potential sabotage targets and adequate physical security measures are mandatory.

For “open” compounds, or those with a “lean-to” roof, the site boundary is to be of “chain-link” fencing, or similar; to approximately 1.8 m height, or to the roof line, as appropriate.

Gates or doors shall be of similar construction, and all parts of the fencing and gates/doors shall be earthed. Gates/doors shall give direct access to the filling connections on the storage tanks. The main gate should have two wings, at least 0.6 m wide.

The storage tank area shall have a second emergency exit gate/door, with one single wing, at least 0.8 m wide. All emergency exits are to open in the direction of escape and are to be fitted with panic furniture of a type not requiring a key, card or code to open. They are to provide an unobstructed means of escape and in operation are not to obstruct any other escape route. Where this communicates with the liquid oxygen (LOx) charging bay, or other enclosed structure, a sill of approximately 150 mm high shall be fitted to prevent spillage from migrating into the enclosed area.

For fully enclosed facilities, e.g., blast-proof shelters, forced ventilation at ground level shall be provided to ensure that an accumulation of vapour does not occur.

Vehicle Access. The approach road(s) shall be designed for use by articulated vehicles and will be required to allow easy access and egress to the storage tanks at all times.

Sufficient space shall be provided to ensure unimpeded freedom of movement between the delivery tanker and the controls of the installation. The delivery tanker will require close access to the refill point on the tank. An 'access apron' of concrete is required beneath the area where the rear of the tanker will be parked. Further information is detailed within BCGA CP 36.

The liquid transfer area shall be designated a 'No Parking' area.

Protective barriers (kerbs, bollards etc.) are to be installed around the tank to prevent any possibility of a collision between the storage tank and the tanker.

There shall be sufficient space to allow a cryogenic liquid replenishment trolley to be connected to the appropriate outlet from the storage tank(s) for filling purposes.

Cryogenic Liquids Boil-off Pit. The boil-off pit is a dedicated area provided to facilitate the safe evaporation of a spillage of cryogenic liquid. It is not intended to contain the contents of a bulk storage tank that has failed catastrophically; and it is not constrained to hold 110% of the cryogenic tank capacity. It should, however, be of sufficient surface area to accommodate any foreseeable spills.

The boil-off pit shall be constructed from oxygen-compatible non-porous materials that will not shatter due to brittle-fracture, such as concrete or coarse gravels, to provide a shallow high-surface-area “pit” to allow heat exchange and evaporation of the cryogenic liquid. Bitumen, tar, asphalt, or other incompatible materials shall not be used.

The boil-off pit shall be sited where it will not cause a hazard to people in adjacent buildings; and be located away from windows and doors, especially emergency exits.

The boil-off pit is to be subjected to regular inspection / maintenance to ensure it is free from contaminants. It shall be kept clear of carbonaceous materials, such as fallen leaves, oils, fuels, or greases, etc. There is the potential for a build-up of water within the boil-off pit. An appropriate means of draining water from the boil-off pit is to be installed.

The boil-off pit shall be totally independent of all soakaways intended for intercepting fuel spillages and surface run-off from aircraft aprons and runways.

This boil-off pit is potentially hazardous when in use, and may fall within the scope of a Confined Space (refer to Annex A to this Chapter and JSP 375). Dependent upon foreseeable spillages, access may need to be restricted by means of barriers, such as chain link fencing and/or the provision of suitable safety signs and warning notices.

As this, the boil-off pit could be used for both liquid oxygen and other liquefied gases, such as nitrogen, argon, or carbon dioxide, the main hazard may vary, depending on which cryogenic liquid was previously discharged, the quantity discharged and the time when it was discharged. The hazard may vary from no hazard, to a vigorous fire hazard, to an asphyxiation hazard, and both an asphyxiation and a toxic gas hazard.

Material Compatibility. In the case of oxygen producing plants, liquid oxygen and liquid nitrogen storage tanks, or cryogenics workshops, no combustible material in significant quantity shall be permitted in the construction of buildings or for permanent fittings or furniture.

Wooden flooring, roofing or partitioning shall not be used. Wood absorbs oxygen and over time the concentration of oxygen held within wood can increase beyond safe limits. Wooden fittings, e.g., workbenches and cupboards, are not to be used. To assist with fire retardance, the use of plasterboard walls in the construction of buildings is not recommended. Walls are to be of solid construction. Internal rough brick/block walls are to be coated with a gypsum or lime-based plaster finished to a smooth surface. Repairs to damaged plasterwork with proprietary cellulose fillers is not recommended.

Any hydrocarbon oil is hazardous in the presence of oxygen, as it is likely to burn spontaneously and with excessive violence. Asphalt, or similar tar-based materials (e.g. bitumen), shall not be used for flooring as these materials, once exposed to liquid oxygen spillages, may detonate on impact. Asphalted surfaces and joints containing asphalt shall not be admissible. A clean non-porous concrete surface with joints containing a silicone filling will be suitable.

Only inert, inorganic, non-porous materials approved for the purpose shall be used for thermal insulation, even temporarily, of liquid oxygen and liquid nitrogen equipment.

All materials in direct contact with cryogenic liquids are to be approved for use with that cryogenic liquid and shall be ‘oxygen compatible’.

Jointing Materials. Joints in cryogenic liquid systems should preferably be made metal to metal.

The use of plastic or fibre, but not asbestos, sheet jointing material is permissible for liquids other than oxygen and nitrogen.

Only oxygen compatible polytetrafluoroethylene (PTFE) tape, to BS 7786, may be used for cryogenic liquid systems. The use of PTFE tape is to be kept to the minimum necessary. Approved PTFE tape is detailed in Table 11.2.

Table 11.2 - Approved PTFE Tape
Description	Support Authority	NSN
Tape, anti-seizing	AC PT	71A/8030-99-5624616

Sealing compounds are unnecessary and shall not be used.

Hoses and Hose Couplings. A hammer shall not be used on hose couplings or fittings when cold. The correct ‘C’ spanner shall be used. If further force is required a mallet may be used to strike the ‘C’ spanner. This method avoids fracture of the metal due to temporary embrittlement.

Joints shall not be tightened unduly when the parts are cold in an endeavour to rectify leakage of liquid.

Oil, grease or lubricants shall not be used with any equipment which comes into contact with liquid oxygen or liquid nitrogen. Storage and transfer equipment used for liquid oxygen is identical to that used for liquid nitrogen, apart from the end couplings, and a hazard would be created by the use of these substances.

On completion of use, all independent hoses shall be emptied of cryogenic fluid, vented and blanked. They shall be hung up and stored in a dry environment. All reasonable action shall be taken to prevent contamination.

Before use, carry out an inspection of the hose/couplings for their serviceability, in particular, ensure the hose/couplings are free from contamination.

Pressure Gauges. All pressure gauges used with liquid or gaseous oxygen equipment shall have dials inscribed ‘OXYGEN’ and ‘Tested without Oil’ or ‘Oil Free’. No other gauges shall be used. (Refer to Figure 11.1 for example).

Figure 11.1 - Approved Oxygen Only Pressure Gauge

Equipment associated with the transfer of gaseous or liquid oxygen shall be kept scrupulously clean and completely free from oil or grease.

Parts accidentally contaminated shall not be used until cleaned by an approved process and certified safe by a competent person.

Pressure gauges cannot be effectively cleaned and if contaminated they shall be removed and replaced with serviceable items.

Emergency Shower. Cold water is a simple and effective means of rapidly conveying heat to parts of the person affected by contact with cryogenic liquid. A drench type, platform operated, emergency shower, complete with eye bath shall be installed at all cryogenic storage facilities.

An automatic- operation alarm system shall be attached to the shower and connected to the Main Guardroom or PBX and Station Medical Centre to alert emergency personnel.

The use of the shower, and the response provided by the emergency services, is to be included in unit Standard Operating Procedures and regularly checked. There is to be clear responsibility for the inspection, testing and maintenance of the shower. Routine maintenance is to include:

  1. A monthly visual inspection, flush, verification of proper operation and testing of the alarm system.

  1. Annual cleaning, inspection and a compliance assessment.

The water supply is to be clean and potable. When activated the water flow is to be continuous and has to be able to maintain a flow for a minimum of 15 minutes. As these showers may be located outside, there is the possibility that water may freeze in the shower operating head or pipelines during cold weather conditions. To prevent freezing of the water, the water supply shall be maintained above freezing but below 20°C.

Water maintained at a temperature between 20 and 45°C has the potential to allow the bacteria Legionella to grow. The hazard from this bacteria is to be assessed, and is to be included in the risk assessment JSP 375, Part 2, Chapter 32 refers for the use of the emergency shower.

The shower shall be positioned such to avoid impeding the normal operations carried out in the Bay or restrict any of the doors. Access to the shower is to be free of any obstructions which may hinder personnel when using the shower in an emergency situation. Provision shall be made to enable the water to drain away freely from the shower area. Drainage of the shower shall be carefully considered, since use of the shower during cold weather may present a hazard due to the formation of ice.

A relevant symbol, or pictogram, shall be clearly displayed, in accordance with the Health and Safety (Safety Signs & Signals) Regulations 1996 Safety Signs and Signals, to indicate that it is an emergency shower. All pipelines are to be clearly identified with their contents. Identification marking of pipelines is to comply with BS 1710.

Figure 11.2 - Example Emergency Shower Sign

Oxygen detection systems. An oxygen detector system shall be fitted in all enclosed buildings to detect and warn against high (oxygen enrichment hazard) and, where appropriate, low concentrations (asphyxiation hazard) of oxygen. The oxygen detector system shall be subject to routine maintenance and calibration to ensure its serviceability. Records of in date calibration shall be held by the operator. These checks shall, as a minimum include visual inspection and functional testing of sensors and alarm systems.

The positioning and number of oxygen detection sensors will be dependent on several factors and will be subject to the requirements of the Risk Assessment for the building (e.g. persons at risk, where the gases may accumulate, what gases present a risk). The maximum oxygen level allowed is 23.5%. The minimum oxygen level allowed is 19%. If these limits are exceeded the area shall be evacuated and appropriately ventilated. Oxygen detection systems shall be sited so they are clearly visible to personnel before entering the affected area.

Notes:
1. Levels of oxygen of 30% and above are of extreme hazard.
2. Excessive levels of oxygen may affect the continued accuracy of the oxygen sensor.

The oxygen detection system shall provide audible and visual alarms within the immediate area. It shall be connected into the extraction system to allow automatic operation. It is recommended that the alarm system be fitted into the main guardroom or PBX to alert the emergency services. Standard Operating Procedures are to be written and enforced detailing the actions to be taken when an alarm sounds by the bay personnel, as well as by other departments and the emergency services. Local emergency services personnel are to be advised on the hazards contained within the bay.

Secondary oxygen detection system. Where the Risk Assessment identifies likelihood that oxygen levels will fluctuate whilst working in an enclosed area, it is recommended that all personnel who require access to the enclosed area are also provided with personal oxygen monitors.

Ventilation. All enclosed working areas shall have ventilation to the outside at ground level. This may take the form of louvered doors.

Where there is the potential for oxygen limits to exceed their ambient levels then an extraction system shall be fitted in the locations where enriched oxygen may be vented, suitable warning notices are to be displayed advising personnel of the hazard.

For blast proof shelters, forced air ventilation shall be provided and fan motors shall conform to current electrical legislation.

The extraction system shall be connected to an oxygen detection system, which automatically operates when high levels of oxygen are sensed.

NATO Standard AAGSP-08 (STANAG 7175) recommends that, to prevent oxygen-enrichment the ventilation should be such as to give an air change of three to five times per hour.

Note: Consideration should be given to providing inlet vents at ceiling level to provide ingress of air.

Earthing. All metal fitments in the facility, including fencing, gates, tanks and all pipe work, shall be adequately earthed. This shall be in accordance with BS 7430 Code of practice for protective earthing of electrical installations.

Pipelines shall be electrically continuous through all connections.

The LOx Super Insulated Vacuum Line (SIVL) or gaseous oxygen supply pipeline shall not be used as earthing routes for other equipment.

All earthing and lightning points bonded to earth, using earthing plates, electrodes, etc, are not to be located in cryogenic liquid boil-off pits, other soakaways, or in areas where they are likely, so far as is reasonably practicable, to come into contact with cryogenic liquids.

## Cryogenic Compounds - Signage

Safety Signs and Warning Notices. These shall be clearly displayed on or near the storage tanks, particularly at access points and are to be visible at all times. The relevant symbols, or pictograms, shall also be clearly displayed in accordance with the Health and Safety (Safety Signs & Signals) Regulations, 1996 Safety Signs and Signals, and with BS EN ISO 7010 (Graphical symbols. Safety colours and safety signs. Registered safety signs). All installations are to comply with the relevant requirements for safety signs and warning notices detailed in Part 2, Chap 9. The following requirements are specific for cryogenic storage sites.

For all cryogenic liquid storage sites:

  1. NO SMOKING

  1. NO NAKED LIGHTS

  1. NO STORAGE OF OIL, GREASE OR COMBUSTIBLE MATERIALS

  1. EXTREME COLD HAZARD

  1. AUTHORISED PERSONS ONLY

  1. NO MOBILE PHONES

  1. NO STEEL TIPPED SHOES / BOOTS

For oxygen storage facilities:

  1. LIQUID OXYGEN

  1. OXIDISING SUBSTANCE

For nitrogen and argon storage facilities:

  1. LIQUID NITROGEN or LIQUID ARGON (as appropriate)

  1. ASPHYXIATION HAZARD

At the entrance to the site the appropriate fire signs and notices (e.g. Fire Action Notice) are to be displayed. A sign shall also be displayed detailing any specific action to be taken in the event of an incident/emergency and showing whom to contact in the event of an incident/emergency with all appropriate contact details. This is to include the unit emergency contact details and the contact details for the cryogenic gas supplier and the cryogenic gas supplier’s 24-hour emergency contact telephone number. The location of any access keys, as well as the contact details for the authorised key holder shall be displayed.

The following signs and pictograms are specific to cryogenic liquids storage areas.

Figure 11.3 - Examples of Cryogenic Signs

Each individual bulk storage tank is to be clearly labelled with its contents and its associated UN product identification number. These are:

  1. LIQUID OXYGEN	UN 1073

  1. LIQUID NITROGEN	UN 1977

  1. LIQUID ARGON	UN 1951

The connection fittings of multi storage installations, pipework connecting storage tanks to equipment or long fill lines are to be clearly marked with the gas name or symbol. Marking and labelling is to be at the inlet and outlet and at approximately 2 m intervals along the length of the pipework. Identification marking of pipelines is to comply with BS 1710.

All displayed safety signs and notices are to be kept legible, visible and up-to-date at all times.

## Cryogenic Compounds - Fire Safety

Fire protection. First aid firefighting equipment comprising water hose reels and / or dry powder extinguishers shall be available. The type and quantity of the firefighting equipment will depend on the size of the installation. The regional Defence Fire & Rescue Service Fire Safety Officer should be consulted about appropriate equipment and its location within the site. A Fire Safety Risk Assessment is to be carried out on all storage sites and is to be incorporated into the Site Fire Safety Management Plan.

The emergency services are to be made aware of the hazard stored within these areas and in the event of a fire or other incident/emergency the response provided by the emergency services, is to be included in the unit Standard Operating Procedures and regularly checked.

Fire Precautions. Smoking, sparks, welding/flame cutting, or naked lights shall not be permitted in the vicinity of oxygen producing or compressing plants, liquid oxygen storage tanks or any activity involving the transfer of gaseous oxygen or liquefied oxygen or nitrogen[10].
[10] Chapter 12 Para’s 39, 40 and 41 refers.

Loose materials, combustible or otherwise, shall not be permitted to remain on liquid oxygen / nitrogen producing or storage sites.

Ready means of entry and exit shall be provided throughout the Cryogenic compound.

Leak Detection. The method of leak detecting shall be in accordance with instructions given in Part 2, Chap 7. Leakages of liquid involving spillage can be readily located by inspection, i.e., the presence of frost and/or ice at the point(s) of leakage.

## Cryogenic Compounds - Bulk Cryogenic Storage Vessels

Owner’s responsibilities for cryogenic bulk storage vessels. Operators who lease cryogenic storage vessels from a Contractor should note that there are different maintenance and operating regimes (e.g., sampling regimes, demarcation of maintenance responsibilities).

Storage vessels, with the exception of those operating below 0.5 bar, or having a pressure-volume product below 250 bar-litre are subject to the Pressure Systems Safety Regulations, 2000 Pressure System Safety Regulations, and/or the Transportable Pressure Vessels Regulations, 2001 Transportable Pressure Vessel Regulations

These regulations place responsibilities on the user of an installed system or on the owner of mobile equipment. An exception is made in respect of equipment that is leased or hired to a user; in this case the supplier of the hired equipment is allowed to take on some of the duties of the user, for the period of the lease (refer to BCGA CP 34).

The cryogenic bulk storage tanks listed in Table 11.3 are MOD owned; and they are maintained by the MOD in accordance with the relevant publication. Further information can be obtained from the relevant Support Authority.

Site and Access Requirements. Bulk storage tanks are usually filled directly from a delivery tanker managed and operated by a MOD contractor (for further details contact Team LEIDOS Lubes and Gases Inventory Manager) thus, adequate provision shall be made for road access and egress of these delivery tankers.

General responsibility for cryogenic bulk storage vessels. All users, operators and fillers of cryogenic storage tanks have a duty of care to ensure that the equipment is maintained correctly and operated safely. Routine checks shall ensure that the equipment remains in a safe condition and is fit for further use. These checks shall, as a minimum, include:

              1. A check for any damage to the tank or installation.

  1. That gas is not venting from any part of the tank surface or from any connections to it.

  1. A check for abnormal frosting on the tank surface.

  1. Relief valves are not continually venting.

  1. Lifed safety devices including pressure relief valves are in date.

  1. The pressure and contents indicating devices are functioning correctly.

Any concerns over the safety of a storage tank, or any defects identified, are to be reported to the owner of the storage tank or the support authority responsible for that tank.

MOD owned cryogenic bulk storage vessels. Details regarding the storage capacities and the associated reference publications for, MOD-owned, liquid oxygen (LOx) and liquid nitrogen (LiN) bulk storage tanks are given in Table 11.3.

Table 11.3 - MOD owned LOx/LiN storage tanks
Storage Tank	Mk. No.	Publication No.
2400 litre	MK 1	DAP 119L-0507-123 / DAP 119L-0507-123
2400 litre	MK 2	DAP 119L-0508-123 / DAP 119L-0508-123
9000 litre	-	DAP 119L-0505-1 / DAP 119L-0505-1

The Support Authority for this equipment is the AC PT.

The Gas Supplier has a duty of care to the User as well as their own employees (driver / filler) to ensure the Users (MOD) tank can be safely filled. The Gas Supplier has the right to conduct a visual inspection and a safety and technical risk assessment of the Users tanks. The technical risk assessment will require information and documentation about the tank to be supplied by the User (the User may need to obtain this information from the Tank Owner- AC PT, or the authorised maintainers General Engineering Flight, Ground Support Equipment section maintainers as applicable).

1. If a Gas Supplier believes a User’s tank is unsafe to fill, they shall:
  1. refuse to fill the tanks,

  1. advice the users of their concern,

  1. suspend future deliveries until the tank is safe to fill.

If a Gas Supplier believes a tank is unsafe to fill because they have identified a safety issue that would not be evident to another Gas Supplier (during their safety and technical assessment before their initial fill of the tank with a product), for example, an overpressure event, the Gas Supplier shall:

  1. advise the User of the immediate actions to take to make the tank safe,

  1. advise the User of the subsequent steps to take the tank out of service,

  1. complete and submit the BCGA Report Form A iaw BCGA CoP 48 Appendix 2.

BCGA will take the following actions:

  1. On receipt of the form, BCGA will contact the User and FGSR to confirm that they are aware of the safety issue, to ascertain if they agree with the findings of the Gas Supplier and to determine if the User is implementing corrective measures.

  1. The BCGA will simultaneously communicate to other Gas Suppliers that this is an unsafe tank to fill.

  1. Inform the Health & Safety Executive (HSE), as appropriate.

The BCGA may further engage with the User to offer advice, as appropriate, with the aim of assisting them in making the tank compliant and safe to fill. If the deficiency is corrected to the satisfaction of a Gas Supplier, deliveries may recommence. The Gas Suppliers’ technical person shall inform the BCGA accordingly.

NOTE: These actions are the gas industry requirements that a Gas Supplier shall carry out, as it is their members / civilian gas delivery drivers who have been placed at risk by MOD (Users) vessels having been identified as unsafe. These actions will be carried out by the civilian Gas Supplier, irrespective of what remedial action carried out by the MOD WRT vessel investigation and repair

Dedication of storage tanks to particular products. A particular bulk storage tank shall be dedicated to one particular cryogenic product and shall be clearly labelled to show the contents and the hazards associated with that product.

It shall not be used for the storage of another cryogenic product, unless the tank has been specifically designed to hold the other product, specific authorisation has been obtained from the relevant Support Authority, and the tank is correctly labelled to identify the contents. In this case a full written Risk Assessment by a Competent Person, to include purging, flushing, cleaning, re-testing and re-labelling shall be carried out before it is put back into service.

Contractor owned cryogenic bulk storage vessels. Team LEIDOS Lubricants and Gases Inventory Manager is working with its contractor to supply a range of bulk storage vessels as requested by the respective Operating Authority. These are available from 25 litre capacity, upwards.

Where Contractor Owned Cryogenic Bulk Storage Vessels are located at a Unit the responsibility for maintenance, periodic examination, replenishment and the quality of the product will remain with the contractor. The contractor is required to provide comprehensive identification of the product and its hazards.

The contractor is required to provide the unit with:

  1. A set of Standard Operating Procedures, detailing the operation of the vessel and a step-by-step procedure for withdrawing the product.

  1. Instructions on the actions to be taken in the event of an emergency or an incident.

  1. Full contact details of a responsible person(s) within the contractor’s organisation.

  1. Initial training on the operation of the vessel.

  1. Certification of the quality of the product.

  1. Provision of technical advice, as required.

  1. Identification of the exact point at which the contractor’s responsibility ends and the MOD / Defence Estates responsibility begins.

For aviation/missile supplied cryogenic fluids the contractor is to sample the product and provide a Certificate of Conformity on a monthly basis see Part 2, Chap 6.

The unit is responsible for managing the vessel on a day-to-day basis and ensuring compliance with the contractors Standard Operating Procedures.

The unit is responsible for ensuring that new / replacement operating staff receives adequate training on contractor owned vessels and associated infrastructure by the contractor.

Sampling and Testing of Product. The sampling, testing and purging requirements for liquid oxygen, used for breathing, and liquid nitrogen, used for aircraft and missile systems, are given in Part 2, Chap 6.

Users’ shall obtain Certificates of Conformity for liquid oxygen used for breathing against Defence Standard 68-284; and for liquid nitrogen, used for aircraft and missile systems, against Defence Standard 58-96.

These Certificates of Conformity shall be kept as evidence of quality control of these products

Replenishment of cryogenic bulk storage vessels. Some contractor-owned bulk storage vessels are being supplied with an approved solar-powered mobile phone permanently fitted to the bulk cryogenic storage vessel to monitor the tank’s contents, on a daily basis; thereby passing responsibility for replenishment to the contractor. Where the provision of such devices is not acceptable, due to Tempest or phone frequency concerns, the unit will be responsible for ordering replenishment stocks. However, whilst this system should maintain tank levels under normal usage, the unit will remain responsible for placing demands with the supplier to cover ad hoc surge demands.

Unless periodic maintenance is due, the contents of in-use bulk storage tanks are to be maintained to at least 25% of the tank capacity. This will help to prevent a build-up of contamination and reduce the need for purging. If a tank capacity falls below 25% then the actions detailed in Part 2, Chap 6, shall be followed.

All units who replenish bulk storage vessels for cryogenic liquids shall have Standard Operating Procedures in place for the receipt of the cryogenic liquid. This is to include a responsible person who can complete the appropriate paperwork and account for the delivery.

Delivery of cryogenic liquid shall only be received from approved MOD Contractors. Advice on approved contractors is available from Team LEIDOS Lubes and Gases Inventory Manager. The contractor’s driver is to make contact with the unit Fuel & Lubricants (F&L) section prior to any delivery taking place.

There shall be a minimum of 3 persons present during bulk replenishment. This shall be the vehicle driver/operator and 2 competent MOD personnel, one MOD person to oversee the receipt and one to act as a safety rating. All persons involved in replenishment shall be competent to do so, they shall have suitable training and they shall wear the appropriate Personal Protective Equipment. Appropriate safety/warning signs shall be displayed during the replenishment.

The training provided is to include the actions to be taken (when safe to do so) to stop the flow of cryogenic liquid from a cryogenic storage tank or cryogenic delivery tanker. Where fitted this includes the operation of the ‘Emergency Stop’ button.

As a result of investigations by the European Industrial Gases Association; the gas industry has fitted electrically operated safety valves to their LiN storage tanks which, when connected to a road delivery vehicle, prevent a tank from over-pressurising during fill. The safety valve is connected to the replenishing delivery vehicle by means of a “flying lead” and should over-pressurising occur, the safety valve will cut the power to the replenishing tanker motor (Please refer to EIGA Doc 151/15 EIGA Doc 151/15 Prevention of Excessive Pressure During Filling of Cryogenic Vessels).

MOD owned LiN storage tanks do not have electrically operated safety valves fitted. It is the user’s responsibility to ensure that LiN is receipted safely. The receipt of LiN into pre modified storage tanks shall be risk assessed and mitigated using appropriate operational and engineering solutions (e.g., use of safety man, and provision of High-Pressure Dummy Socket (HPDS) fitted to the delivery vehicle’s flying-lead). The process shall be authorised by the relevant duty holder.

Before delivery, check the cryogenic liquid is the correct product and it is to the specification and standard required. Refer to the Certificate of Conformity, Part 2, Chap 6.

Ensure that the delivery vehicle is correctly positioned. Check that the coupling end of the delivery hose is free from contamination. Ensure that the delivery vehicle, supply hoses and receiving vessel are suitably earthed and ensure no activities, with the potential to cause a spark, are taking place within 25m of the replenishment.

Ensure that the tank to be filled is an approved vessel for storing cryogenic liquid, and that the vessel is serviceable.

All delivery vehicles should be fitted with an Emergency Stop button. All persons involved in replenishment are to be familiar with the location of this button and the actions to be taken if an emergency situation arises. Establish an agreed code of signals and /or verbal communications with the driver to ensure the delivery process can be halted immediately should any incident jeopardise the safety of personnel or equipment.

At the end of the replenishment, check the quantity of product delivered. Receive a Certificate of Conformity for the product. Complete the delivery note and sign the MOD Form 640 as appropriate, guidance can be found at JSP 462.

## Bibliography

British Compressed Gases Association (BCGA) Publications

            1. BCGA CP 34 The Application of the Pressure Equipment Regulations to Customer Sites.

            1. CP26 - Code of Practice: Bulk Liquid Carbon Dioxide Storage at Users’ Premises.

            1. CP27 - Code of Practice: Transportable Vacuum Insulated Receptacles of not More than 1000 Litres Volume.

CP30 - Code of Practice: The Safety Use of Liquid Nitrogen Dewars up to 50 Litres.

CP36 - Code of Practice: Bulk Cryogenic Liquid Storage at Users’ Premises.

British Standards

BS 1710 – Specification for Identification of Pipelines and Services.

BS EN 62305-1:2011 - Protection against lightning. General principles.

BS 7786 - Specification for Unsintered PTFE Tapes for General Use.

BS EN 1057 - Copper and Copper Alloys – Seamless, Round Copper Tubes for Water and Gas in Sanitary and Heating Applications.

BS EN 12449 - Copper and Copper Alloys – Seamless, Round Tubes for General Purposes.

BS EN 60529 - Specification for degrees of protection provided by enclosures (IP Code).

BS EN 12464-1:2011 - Light and lighting. Lighting of work places. Indoor work places.

BS 5429 - Code of Practice for Safe Operation of Small-Scale Storage Facilities for Cryogenic Liquids.

BS 7430:2011+A1:2015 - Code of practice for protective earthing of electrical installations.

Health and Safety Executive

            1. EH40: EH40 – Workplace Exposure Limits: Containing the List of Workplace Exposure Limits for Use with the Control of Substances Hazards to Health Regulations, 2002 (as amended).

UK Legislation

            1. Safety Signs and Signals: SI 1996. No. 341 - The Health and Safety (Safety Signs and Signals) Regulations, 1996.

            1. Confined Space Regulations: SI 1997 No. 1713 - The Confined Space Regulations, 1997.

            1. Pressure System Safety Regulations: SI 2000 No. 128 - Pressure Systems Safety Regulations, 2000.

            1. SI 2001 No. 1426 - Transportable Pressure Vessels Regulations, 2001.

            1. Carriage of Dangerous Goods and Use of Transportable Pressure Equipment: UK Statutory Instruments 2020 No. 1111, The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment (Amendment) (EU Exit) Regulations 2020

            1. DSEAR: SI 2002 No. 2776 - The Dangerous Substances and Explosive Atmospheres Regulations 2002

            1. Directive 2014/34/EU: DIRECTIVE 2014/34/EU OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL of 26 February 2014 on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres (recast)

MOD Documents

            1. DAP 107D-0001-1DAP 107D-0001-1 - General Information on Aircraft Oxygen Equipment.

            1. Defence Standard 58-96 - Pure Gases for Weapons Systems and Detector Cooling Applications.

            1. Defence Standard 68-284 - Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications.

            1. JSP 375: JSP 375 - Management of Health and Safety in Defence.

            1. JSP 515: JSP 515 - MOD Hazardous Stores Information Systems.

            1. MOD Form 640 - Advice and Inspection Note

NATO Documents

            1. STANAG 7175 - Definition of Safety Zones and Minimum Separation Distances for Use With Liquid Oxygen (LOx).

# Annex A - Inert Gas Asphyxiation

            1. Table 11.A.1 provides a summary of the effects of various depleted oxygen concentrations. It is important to note that these effects and symptoms can occur within a relatively short time, without the person’s knowledge and without prior warning (refer to the Confined Space Regulations and JSP 375, Part 2, Chap 28).

            1. The following example shows how a spillage of an inert cryogen, such as liquid nitrogen, could give rise to oxygen deficiency.

            1. Example 1: Assume a full 25 litre Dewar of liquid nitrogen is stored in a small room 3m by 3m by 3m; and that the original concentration of oxygen in the room was 20.95%.

            1. If this liquid was spilt the following consequences may occur:

  1. Volume of room = 3 x 3 x 3 = 27 m3.

  1. Volume of spilt gas (nitrogen) = 25 litres x 682(682 is the nitrogen - volume of Gas to Volume of Liquid ratio, see Table 12.1)” = 17050 litres = 17.05 m3.

  1. This 17.05 m3 of nitrogen gas displaces 17.05 m3 of air from the room, replacing it with nitrogen.

  1. The oxygen content of the room becomes reduced to the volume: (27 – 17.05) m3x 0.2095 = 2.08 m3”

  1. The resulting oxygen content of the room is now: 100 x 2.08 / 27.0 = 7.7%.

  1. From Table 11.A.1, this will result in fainting within a few minutes; resuscitation is possible if carried out immediately, i.e. someone is on hand with a self-contained breathing apparatus to remove the person(s) from the room.

Table 11.A.1 - Effects of oxygen deficiency
Oxygen Content (volume %)	Effects and Symptoms (at atmospheric pressure)
21 - 14	Increasing pulse rate, tiredness
14 -11	Physical movement and intellectual performance become difficult
11 - 8	Possibility of headaches, dizziness and fainting after a fairly short period of time
8 - 6	Fainting within a few minutes, resuscitation possible if carried out immediately
6 -0	Fainting almost immediate, death or severe brain damage.
Note: Remember this happens within a relatively short time, without the person’s knowledge and without prior warning.

# 12 - Cryogenic Liquids

Chapter Sponsor - CGMS DECA Stafford

## Scope

            1. This chapter is concerned with cryogenic liquids when stored in MOD owned cryogenic storage tanks (vessels) and Contractor owned bulk storage vessels sited in MOD Cryogenic enclosures. It discusses the properties of and the hazards associated with the storage and use of cryogenic liquids; the properties of cryogenic storage vessels, both pressurised and non-pressurised.

## Properties and Hazards of Cryogenic Liquids, General

            1. Bulk gases are purchased in units of hundred cubic metres (HCMs), referenced to standard conditions. In the UK these standard conditions are 15°C and 1013.25 millibar pressure. A HCM is one hundred cubic metres (100m3) of gas: equivalent to 100,000 litres of gas. The corresponding volume, in litres, of one HCM of a particular cryogenic liquid is therefore 100,000 divided by the volume of gas to volume of liquid ratio (refer to Table 12.1). e.g.

              1. 1.0 HCM of gaseous oxygen = 118.76 (=100000 / 842) litres of LOx.

              1. 1.0 HCM of gaseous nitrogen = 146.62 (=100000 / 682) litres of LiN.

Table 12.1 - Properties of cryogenic liquids (and associated gas)
Property	Oxygen (O2)	Nitrogen (N2)	Argon (Ar)	Carbon Dioxide (CO2)
Molecular Weight.	32	28	40	44
Colour of Gas	None	None	None	None
Colour of Cryogenic liquid.	Light Blue	None	None	None
Paramagnetic	Yes	No	No	No
Normal Boiling Point at atmospheric pressure. (ºC)	–183	–196	–186	–78.5 (Sublimes)
Critical Temperature. (ºC)	–118.4	–147	–122	+ 30.1
Ratio: Volume of Gas to Volume of Liquid, measured at +15°C and 101.3 kPa (absolute).	842	682	822	845 (solid)
Relative Density of Gas, at 101.3 kPa, 25°C (absolute) (Air = 1).	1.105	0.967	1.380	1.48
Liquid Density, at 101.3 kPa (absolute). (kg/m3)	1141	807	1394	1030
Latent Heat of Evaporation. (kJ/kg)	213	199	161	573 (Sublimes)
Respiration difficulties due to vapour inhalation	Yes	Yes	Yes	Yes
Asphyxiant	No	Yes	Yes	Yes
Toxic	No	No	No	Yes
Supports Life	Yes	No	No	No

            1. General Safety Precautions. Before carrying out any work with cryogenic gases, Users must be aware of:

The Hazards and the Safety Requirements associated with the storage, transfer and use of cryogenic gases.

The selection and use of necessary Personal Protective Equipment, (PPE), (refer to Part 2, Chap 2).

Wet gloves shall not be used when operating with cryogenic products. Contact with materials which are at very cold temperatures, such as valves, hoses, etc. can cause wet gloves to get very cold and potentially freeze, restricting mobility and providing no protection to the wearer. Where gloves are considered necessary, more than one pair of gloves shall be provided such that dry equipment is always available.

            1. General information on aircraft oxygen equipment is given in DAP107D-0001-1.

            1. Critical Temperature. All gases can be liquefied if cooled to a sufficiently low temperature. Liquid argon, liquid nitrogen and liquid oxygen are obtained by separating the constituents of atmospheric air liquefied in this way. Above a certain temperature, the Critical Temperature, a gas cannot be condensed or exist as a liquid regardless of the pressure applied (refer to Table 12.1).

            1. Evaporation rate. Heat is required to evaporate liquefied gases; the rate of evaporation being governed by the rate of heat transfer. Thus a liquefied gas in an uninsulated vessel will boil briskly as heat is absorbed from the atmosphere and all the liquid may be evaporated within an hour; whereas, when the liquid is contained in a vacuum-insulated receptacles, i.e. vacuum-insulator evaporator (VIE), vacuum-insulator tank ( VIT), and vacuum-insulator vessel (VIV), it will simmer gently and, according to the capacity of the receptacles, may take many days or weeks to evaporate completely. When spilled on the ground the rate of heat absorption is so great that the liquid evaporates in a few minutes.

## General Class Hazards of Cryogenic Liquids

            1. Principal Hazards. The nature of cryogenic liquids gives rise to two principal hazards: low-temperature effects; and excessive pressure generation in storage vessels and pipelines. Procedures for managing these risks are given in the remainder of this chapter.

            1. Low air temperatures caused by the proximity of liquefied gases and discharges of these gases to atmosphere may cause hypothermia, and people at risk shall be suitably clothed to provide protection against this (refer to Table 12.1).

            1. In addition, the properties of the particular cryogenic liquid must also be considered in respect of the effect of its gaseous product upon respiration, in confined surroundings, as a result of leakage or spillage (refer to Table 12.1 and for the properties of particular cryogenic liquids refer to the respective sections within this Chapter).

            1. Respiration Hazards. Respiration of the gaseous products may give rise to asphyxia in the case of oxygen-deficient atmospheres (refer to Table 12.1). Carbon dioxide, as well as having the potential to produce oxygen-deficient atmospheres, is toxic once its concentration exceeds a few per cent by volume (refer to Table 12.2).

Table 12.2 - Effects of Carbon dioxide inhalation
Carbon dioxide Concentration (Volume %)	Effects and Symptoms
1	Slight and unnoticeable increase in breathing rate.
2	Breathing becomes deeper, rate increases to 50% above normal. Prolonged exposure (several hours) may cause headache and feeling of exhaustion.
3	Breathing becomes laboured, rate increases to twice the normal. Hearing ability reduced, headache experienced with increase in blood pressure and pulse rate.
4 - 5	Breathing laboured at four times the normal. Symptoms as above, with signs of intoxication after ½ hour exposure and slight choking feeling.
5 - 10	Characteristic pungent odour noticeable. Breathing very laboured, leading to physical exhaustion. Headache, visual disturbance, ringing in ears, confusion probably leading to loss of consciousness within minutes. Immediately Dangerous to Life.
Above 10	Loss of consciousness more rapid, with risk of death from respiratory failure. Hazard to life increased with concentration, even if no oxygen depletion. Immediately Dangerous to Life.
Note: It should be appreciated that the reactions of some individuals may be very different from those shown in this table

            1. The body cannot detect oxygen-deficient atmospheres by smell, or other means; and a person entering such an area will be seen by onlookers to simply collapse; hence the former use of canaries in mines.

            1. Respiration of an oxygen-enriched atmosphere is potentially less safe than breathing clean air; and breathing pure oxygen at atmospheric pressure for several hours may produce hallucinatory effects and intoxication of the central nervous system. The most significant hazard, however, for oxygen-enriched atmospheres is the considerable increase in fire risk. Sparks or smoking, which might be regarded as normally harmless, can cause fires that can burn vigorously or explosively in oxygen-enriched atmospheres.

            1. Transient exposure to a very cold gas may produce discomfort in breathing and may provoke an asthma attack in susceptible people.

            1. Prolonged exposure to cold gas can produce serious effects on the lungs.

            1. Heat Transfer Processes. Cryogenic liquids, by reason of their extremely low temperatures (refer to Table 12.1), continuously absorbs heat from their surroundings, there being no perfect heat insulating medium available. This inflow of heat cannot be entirely prevented and in consequence cryogenic liquids must evaporate continuously at a greater or lesser rate according to the heat transfer permitted.

            1. If there is no outlet or safety release provided for the gas, the pressure will rise as evaporation proceeds and a closed receptacle, unless constructed to withstand the ultimate pressure, will eventually rupture. The effect of rupture even at comparatively low pressures could be serious.

            1. It is possible by employing special refrigeration equipment to re-condense the gas evaporated from cryogenic liquid receptacles, and so to maintain supplies without loss. This does not mean that evaporation, as a result of heat flow, can be prevented.

            1. Effect on Materials, including Skin. Cryogenic liquids rapidly extract heat from their immediate surroundings until the temperature is reduced to that of the liquid (refer to Table 12.1). At these temperatures’ ductile metals, rubbers and plastics become brittle and may fail under loading or impact.

            1. If allowed to remain in contact with the skin longer than momentarily, cryogenic liquids cause severe burning or “frostbite”. This can arise through contact with uninsulated surfaces of equipment, which in use become chilled to near cryogenic gas temperatures (refer to Table 12.1). The presence of frost may give an indication of chilling, but in a relatively dry atmosphere this takes time, and a dangerous condition may exist unnoticed.

            1. If a chilled object is accidentally grasped with bare hands the skin will adhere (“freeze”) to the surface and may be torn on removal, so aggravating the injury received.

## Properties and Hazards of Liquid Oxygen

            1. Properties. Liquid oxygen is clear, pale blue in colour, slightly heavier than water, and has no smell. At atmospheric pressure it boils at –183°C, the gaseous oxygen given off occupying about 840 times the volume of the liquid (at +15°C). The gas is slightly heavier than air at the same temperature. In the pure state liquid oxygen is stable. The liquid cannot be detonated by disturbance or shock.

            1. Toxicity. Oxygen is non-toxic at atmospheric pressure, but sustained breathing of pure, neat, oxygen at atmospheric temperature for several hours may produce hallucinatory effects and intoxication of the central nervous system.

            1. The toxicological effects of breathing pure, neat, oxygen under pressure must be considered, particularly in respect of diving and hyperbaric applications.

            1. Fire Hazards. In addition to the general class hazards discussed at paragraph 7-14 of this Chapter, the principal hazard associated with both liquid and gaseous oxygen is fire. A dangerous concentration of gaseous oxygen in the atmosphere can exist undetected. Combustible materials which do not normally burn readily in air would burn fiercely in an oxygen rich atmosphere.

            1. Being heavier than air, especially when cold, as when evaporated from a liquid, the gas has a tendency to linger near floor level and may remain in a pit or a confined space for a considerable time. Combustible material, such as clothing, could be ignited in such an atmosphere. It is conceivable that a strand of material could be ignited by a static electrical discharge for which it formed a path, and thus precipitate combustion of the mass.

            1. Ignition may occur through the inclusion of traces of oil or grease in oxygen systems. While not liable to ignite spontaneously at atmospheric pressure, these substances, if present in the vicinity, could contaminate equipment, such as valve outlets and liquid hose couplings, and later give rise to ignition when conditions become favourable.

            1. Materials, including hair and skin, which burn in air will burn fiercely in oxygen. Some materials, such as metals, which do not burn in air, will burn in oxygen.

            1. Although a necessary constituent of combustion, oxygen is not, in the accepted sense, itself combustible. Once started, combustion in oxygen proceeds until all of the material or all of the oxygen is consumed.

            1. If readily combustible material in finely divided form, e.g., cotton or wool fabric, charcoal, sawdust, etc, is ignited in oxygen, combustion is extremely rapid. If sufficient oxygen is present, a violent explosion will result.

            1. Hydrocarbon based oils and greases are combustible materials which have a high affinity for oxygen. They may ignite spontaneously in gaseous oxygen under high pressure. Even if only a trace of oil or grease is present sufficient heat may be generated under these circumstances to ignite other, less combustible, substances in the surroundings, including the metal of the containing vessel itself.

            1. Explosion. Oils, greases and some other organic materials are liable to spontaneous combustion or explosion in the presence of gaseous oxygen; liquid oxygen is less hazardous in this respect. Its low temperature implies low intrinsic physical energy for spontaneous effects, but certain organic materials soaked in liquid oxygen are prone to detonation by the energy of impact. This is considered to result from the formation of unstable compounds which release explosive energy on impact. Inorganic materials such as aluminium, carbon and iron in finely divided form, are also known to explode when soaked in certain proportions of liquid oxygen.

            1. Pure oxygen is outside the scope of the definition of explosive atmosphere. However, where oxygen or other oxidising agents are used, assessment must take into account the hazardous chemical properties. This assessment is best achieved by conducting a Site Risk Assessment IAW JSP 375 Part 2, Chapter 8 - Annex B.

            1. Confined Spaces. Inspection pits, wells, or other Confined Spaces adjacent to an installation holding oxygen shall not be entered without a suitable and sufficient, written, Risk Assessment and/or Permit to Work, to assess whether the work can be done without the need for people to enter the confined space, identify the hazards present, assess the risks and determine what precautions are to be taken (refer to the Confined Space Regulations and JSP 375, Part 2 Chapter 28).

## Properties and Hazards of Liquid Nitrogen

            1. Properties. Liquid nitrogen is clear and colourless, slightly lighter than water, and has no smell or taste. At atmospheric pressure it boils at –196°C, the gaseous nitrogen given off occupying about 682 times the volume of the liquid (at +15°C). The gas is slightly lighter than air at the same temperature.

            1. Toxicity. Liquid nitrogen is chemically inert. It is incombustible and for this reason is an effective fire extinguisher. The gas is non-toxic but is incapable of supporting respiration.

            1. In addition to the general class hazards discussed in paragraphs 7-14 to this Chapter, the principal hazard associated with both liquid and gaseous nitrogen is its inability to support respiration and the production of local oxygen-deficient atmospheres, which will produce asphyxia if breathed.

            1. Free entrance is only permissible if the oxygen concentration is between 20 and 22%. Atmospheres containing less than 18% oxygen are potentially dangerous; and, atmospheres containing less than 10% oxygen can cause brain damage and death (refer to Part 2, Chap 11, Annex A).

            1. Asphyxia due to oxygen deficiency is often rapid with no prior warning to the victim. The body cannot detect oxygen-deficient atmospheres by smell, or other means; and a person entering such an area will be seen by onlookers to simply collapse.

            1. Oxygen-Enrichment of Air. The low-temperatures of bulk liquid nitrogen (and liquid helium) are such that adjacent atmospheric air may become liquefied, giving rise to preferential oxygen-enrichment.

            1. Thermal insulation around liquid nitrogen (and liquid helium) storage tanks and pipe work may become saturated with oxygen-enriched air and possess an enhanced fire hazard. All such thermal insulation shall be oxygen compatible.

            1. For the same reasons, grease and oil contamination shall be prevented; and, where the use of these products is necessary, only approved oxygen-compatible products shall be used.

            1. Confined Spaces. Inspection pits, wells, or other Confined Spaces adjacent to an installation holding liquid nitrogen shall not be entered without a suitable and sufficient, written, Risk Assessment and/or Permit to Work, to assess whether the work can be done without the need for people to enter the confined space, identify the hazards present, assess the risks and determine what precautions are to be taken (refer to Part 2, Chap 11, Annex A, the Confined Space Regulations and JSP 375.

## Properties and Hazards of Liquid Argon

            1. Properties. Liquid argon is clear and colourless, it is heavier than water, and has no smell or taste. At atmospheric pressure it boils at –186°C, the gaseous argon given off occupying about 822 times the volume of the liquid (at +15°C). The gas is heavier than air at the same temperature.

            1. Toxicity. Liquid argon is chemically inert. It is incombustible and for this reason is an effective fire extinguisher. The gas is non-toxic but is incapable of supporting respiration. Being heavier than air, especially when cold, as when evaporated from a liquid, the gas has a tendency to linger near floor level and may remain in a pit or a confined space for a considerable time.

            1. In addition to the general class hazards discussed in paragraphs 7-14 to this Chapter, the principal hazard associated with both liquid and gaseous argon is its inability to support respiration and the production of local oxygen-deficient atmospheres, which will produce asphyxia if breathed.

            1. Free entrance is only permissible if the oxygen concentration is between 20 and 22%. Atmospheres containing less than 18% oxygen are potentially dangerous; and, atmospheres containing less than 10% oxygen can cause brain damage and death (refer to Part 2, Chap 11, Annex A).

            1. Asphyxia due to oxygen deficiency is often rapid with no prior warning to the victim. The body cannot detect oxygen-deficient atmospheres by smell, or other means; and a person entering such an area will be seen by onlookers to simply collapse.

            1. Confined Spaces. Inspection pits, wells, or other Confined Spaces adjacent to an installation holding liquid argon shall not be entered without a suitable and sufficient, written, Risk Assessment and/or Permit to Work, to assess whether the work can be done without the need for people to enter the confined space, identify the hazards present, assess the risks and determine what precautions are to be taken (refer to Part 2, Chap 11, Annex A, the Confined Space Regulations and JSP 375.

## Properties and Hazards of Carbon Dioxide

            1. Properties. Liquid carbon dioxide is clear and colourless, it is slightly heavier than water. At atmospheric pressure, it sublimes at - 78.5°C, the gaseous carbon dioxide given is 845 times of the solid volume at (+15°C). At normal ambient temperature and pressure, carbon dioxide is a colourless gas which is toxic with a slightly pungent odour at high concentrations (refer to Table 12.2). It does not support life or combustion and is heavier than air. It is an effective fire extinguisher. Carbon dioxide will dissolve in water to a limited extent to form a weak acid.

            1. Carbon dioxide is naturally present in the atmosphere at about 0.03% (300 ppm), by volume; this concentration may be higher due to the effects of respiration in confined spaces, combustion processes and the effects of internal combustion engines, such as vehicles.

            1. “Dry Ice”. Solid carbon dioxide is available commercially; it is sometimes known as “Dry Ice”. It sublimes at pressures below 20 bar, i.e., on warming it changes directly from a solid to a gas.

            1. It cannot be overemphasised that the physical properties of “Dry Ice” differ significantly from those of ice, i.e., frozen water. “Dry Ice” has a temperature of –78.5°C, which is low enough to inflict cold “burns”; it has a volume of gas to volume of solid ratio of 845 (at +15°C), which may led to rupture of closed receptacles; at atmospheric pressure it sublimes to produce gaseous carbon dioxide, which is an asphyxiant and is toxic at concentrations above a few percent by volume (refer to Table 12.2); whereas, ice has a normal temperature of 0°C and a volume of solid to volume of liquid ratio of nearly 1.0.

WARNING: “Dry Ice” shall not be used as a direct substitute for ice.

Liquid Carbon Dioxide. Carbon dioxide is usually transported and stored in bulk as a liquefied gas, at a temperature of about –17°C and a pressure above 20 bar. It cannot exist as a liquid at atmospheric pressure.

When liquid carbon dioxide under pressure is released to the atmosphere, a dense white cloud is formed containing the cold gas, solid carbon dioxide particles and condensed moisture from the air. The solid carbon dioxide particles, at –78.5°C, may settle on adjacent surfaces before subliming to produce more cold gas.

Example of liquid carbon dioxide under pressure bring released into the atmosphere.

Liquid carbon dioxide will change to a solid when the pressure falls below 5.18 bar and may give rise to a risk of a system blockage.

Being heavier than air, especially when cold, as when evaporated from a liquid, the gas has a tendency to linger near floor level and may remain in a pit or a confined space for a considerable time.

Toxicity. In addition to the general class hazards discussed in paragpraphs 7-14 to this Chapter, the principal hazard associated with carbon dioxide is its toxicity; and, its ability to produce local oxygen-deficient atmospheres, which will produce asphyxia if breathed. Table 12.2 provides a summary of the effects of inhaling varying concentrations of carbon dioxide; but it should be appreciated that the reactions of some individuals may be very different from those shown in Table 12.2.

The Health and Safety Executive (HSE) have set Workplace Exposure Limits for carbon dioxide of: 5000 parts per million by volume ppm (v), (or 0.5%vol), Long-term Exposure Limit (eight-hour reference period); and 15000 ppm (v), (1.5%vol), Short-term Exposure Limit (15-minute reference period). (Refer to HSE guidance EH40 EH40 for further details).

Free entrance is only permissible if the oxygen concentration is between 20 and 22% and the carbon dioxide concentration is below its Workplace Exposure Limits. Atmospheres containing less than 18% oxygen, or more than 1.5% carbon dioxide are potentially dangerous; and atmospheres containing less than 10% oxygen, or more than 5% carbon dioxide, can cause brain damage and death (refer to Part 2, Chap 11, Annex A).

Asphyxia due to oxygen deficiency is often rapid with no prior warning to the victim. The body cannot detect oxygen-deficient atmospheres by smell, or other means, although high concentrations of carbon dioxide may be detected by its odour; and a person entering such an area will be seen by onlookers to simply collapse.

Confined Spaces. Inspection pits, wells, or other confined spaces adjacent to an installation holding carbon dioxide shall not be entered without a suitable and sufficient, written, Risk Assessment and/or Permit to Work, to assess whether the work can be done without the need for people to enter the confined space, identify the hazards present, assess the risks and determine what precautions are to be taken (refer to Part 2, Chap 11, Annex A, the Confined Space Regulations and JSP 375).

## Safety Management of Cryogenic Compounds

Operating Procedures. Operators of bulk cryogenic compounds shall produce site specific Standard Operating Procedures (SOPs) that detail all relevant site activities for cryogenic operations. As a minimum, these activities shall include, receipt, issue, blow down, and emergency procedures (or signpost to relevant emergency procedures). The SOPs should not replicate existing policy documents, but shall inform operators of site specific operational and emergency processes IAW BCGA CoP 36.

Personnel Safety. Where possible, clothing contaminated with cryogenic liquids should be removed to lessen the time of contact with the skin. However, no attempt shall be made to remove any clothing that has “frozen” onto the skin.

Alcoholic beverages and smoking are not to be permitted. In the case of liquid oxygen, any degree of personal contamination with oxygen constitutes a grave fire risk to both the injured person and those giving First Aid; and the No Smoking Rule shall be observed as long as the contamination remains.

Safety Man. To ensure that prompt first aid can be rendered, or assistance given in the event of an accident during cryogenic liquid transfer, a ‘Safety Man’ shall be present at all times and wearing full protective clothing during transfer operations.

The safety man is to have had appropriate training in the following areas:

  1. Handling of cryogenic liquids.

  1. Hazards of cryogenic liquids.

  1. First aid (for cryogenic liquids).

  1. Local emergency procedures and actions.

  1. Operation of the equipment.

  1. The use of fire-fighting equipment.

There shall be a minimum of 3 persons present during bulk replenishment. This shall be the vehicle driver/operator and 2 competent MOD personnel, one MOD person to oversee the receipt and one to act as a safety rating. All persons involved in replenishment shall be competent to do so, they shall have suitable training and they shall wear the appropriate Personal Protective Equipment. Appropriate safety/warning signs shall be displayed during the replenishment.

Pressure Release. Attempts shall never be made to confine cryogenic liquids in a vessel or pipe not provided with automatic pressure release equipment, such as a pressure relief valve or bursting disc.

Hoses used to transfer cryogenic liquids between storage and transport tanks shall be vented to atmosphere immediately after the liquid valves of both tanks are closed, to prevent damage by over-pressure. If a manually operated vent valve is not provided, the hose shall be uncoupled; it is not good practice to depend on automatic pressure relief devices which may become temporarily inoperative through icing. The hose shall be drained of liquid before blanks are fitted.

Aircraft servicing hoses shall always be vented when the tank liquid valve is closed between transfer operations by parking the filling connector on the special fixture provide on the trolley.

Automatic pressure relief devices shall be provided on all fixed pipeline installations used for conveyance of cryogenic liquids where sections can be isolated by operation of control valves.

Pressure relief valves shall not on any account be adjusted or tampered with while under pressure in order to rectify leakage. Defective valves shall be removed from equipment for servicing and testing immediately. They are to be replaced with serviceable items.

Storage and Transport. Cryogenic liquid tanks, with the exception of carbon dioxide, are normally maintained freely vented to the atmosphere (or to a gasholder if provided) except when liquid is being discharged.

Liquefied gases cannot be conserved by preventing escape of the evaporated gas since evaporation is controlled by the rate of heat absorption.

When cryogenic liquid tanks are being transported in enclosed vehicles or aircraft, means shall be provided for the safe venting of the evaporated gas, either by adequate ventilation or by directing the vent discharge to the outside of the vehicle or aircraft. When being transported, cryogenic liquids are classified as Dangerous Goods and the receptacles and the cryogenic liquid are only to be transported in accordance with the Dangerous Goods Regulations (refer to Part 2, Chap 8).

Cryogenic tanks or vessels shall not be transported in lifts unless a suitable and sufficient, written, Risk Assessment has been carried out and precautions are put in place to reduce, as low as is reasonably practicable, the risks to personnel and to equipment. Where carriage in a lift is unavoidable, the use of a remotely controlled, unmanned, goods-only lift is the primary choice; otherwise, the lift shall be operated strictly as a confined space (refer to Annex A to Chapter 11), the Confined Space Regulations and JSP 375, Part 2, Chap 28). Any spillages of cryogenic liquids may endanger the life of any personnel inside the lift and compromise the structural integrity of the floor.

Medical First Aid. In all cases of injury from a cryogenic liquid qualified medical assistance is to be called immediately. All cases of injury through contact with cryogenic liquids shall be given medical attention without delay.

All units who use, store or transport cryogenic liquids are to have Standard Operating Procedures in place for dealing with cases of injury through contact with cryogenic liquid. These are to be endorsed by the senior medical officer on the unit. The unit is to carry out a First Aid Assessment with emphasis on the hazard from cryogenic liquid (see JSP 375, Part 2, Chap’s 5 and 14). Any equipment identified in the First Aid Assessment is to be provided and maintained in a serviceable condition. Signage across the site is to clearly identify First Aid equipment locations, the emergency shower and the nominated First Aiders.

Spillages. Avoid spillage of cryogenic liquids:

  1. It may become trapped in pockets, shoes, etc.

  1. Do not tread in spilled cryogenic liquids.

  1. Do not allow vehicles to drive through spilled cryogenic liquids, as this may lead to embrittlement and bursting of tyres.

As spillage of liquid oxygen within a Confined Space will readily lead to an oxygen-enriched atmosphere, clothing will absorb a higher level of oxygen than normal and will burn fiercely if ignited.

Personnel who have worked in such an atmosphere are not to smoke, go near heat sources or naked flames until they have ventilated their clothing by walking about in a normal atmosphere for at least 15 minutes.

Conversely, spillage of liquid nitrogen, liquid argon or liquid carbon dioxide within a Confined Space may lead to the production of local oxygen-deficient atmospheres, which will produce asphyxia if breathed. Asphyxia due to oxygen deficiency is often rapid with no prior warning to the victim. The body cannot detect oxygen-deficient atmospheres by smell, or other means; and a person entering such an area will be seen by onlookers to simply collapse, refer to Part 2, Chap 11, Annex A.

Ensure there are Standard Operating Procedures in place to deal with spillages, fires etc. that have been fully agreed between the site operators and the emergency services.

## Bibliography

British Compressed Gases Association (BCGA) Publications

            1. BCGA CP 34 The Application of the Pressure Equipment Regulations to Customer Sites.

            1. CP26 - Code of Practice: Bulk Liquid Carbon Dioxide Storage at Users’ Premises.

            1. CP27 - Code of Practice: Transportable Vacuum Insulated Receptacles of not More than 1000 Litres Volume.

CP30 - Code of Practice: The Safety Use of Liquid Nitrogen Dewars up to 50 Litres.

CP36 - Code of Practice: Bulk Cryogenic Liquid Storage at Users’ Premises.

British Standards

BS 1710 – Specification for Identification of Pipelines and Services.

BS EN 62305-1:2011 - Protection against lightning. General principles.

BS 7786 - Specification for Unsintered PTFE Tapes for General Use.

BS EN 1057 - Copper and Copper Alloys – Seamless, Round Copper Tubes for Water and Gas in Sanitary and Heating Applications.

BS EN 12449 - Copper and Copper Alloys – Seamless, Round Tubes for General Purposes.

BS EN 60529 - Specification for degrees of protection provided by enclosures (IP Code).

BS EN 12464-1:2011 - Light and lighting. Lighting of work places. Indoor work places.

BS 5429 - Code of Practice for Safe Operation of Small-Scale Storage Facilities for Cryogenic Liquids.

BS 7430:2011+A1:2015 - Code of practice for protective earthing of electrical installations.

Health and Safety Executive

            1. EH40: EH40 – Workplace Exposure Limits: Containing the List of Workplace Exposure Limits for Use with the Control of Substances Hazards to Health Regulations, 2002 (as amended).

UK Legislation

            1. Safety Signs and Signals: SI 1996. No. 341 - The Health and Safety (Safety Signs and Signals) Regulations, 1996.

            1. Confined Space Regulations: SI 1997 No. 1713 - The Confined Space Regulations, 1997.

            1. Pressure System Safety Regulations: SI 2000 No. 128 - Pressure Systems Safety Regulations, 2000.

            1. SI 2001 No. 1426 - Transportable Pressure Vessels Regulations, 2001.

            1. Carriage of Dangerous Goods and Use of Transportable Pressure Equipment: UK Statutory Instruments 2020 No. 1111, The Carriage of Dangerous Goods and Use of Transportable Pressure Equipment (Amendment) (EU Exit) Regulations 2020

            1. DSEAR: SI 2002 No. 2776 - The Dangerous Substances and Explosive Atmospheres Regulations 2002

            1. Directive 2014/34/EU: DIRECTIVE 2014/34/EU OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL of 26 February 2014 on the harmonisation of the laws of the Member States relating to equipment and protective systems intended for use in potentially explosive atmospheres (recast)

MOD Documents

            1. DAP 107D-0001-1DAP 107D-0001-1 - General Information on Aircraft Oxygen Equipment.

            1. Defence Standard 58-96 - Pure Gases for Weapons Systems and Detector Cooling Applications.

            1. Defence Standard 68-284 - Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications.

            1. JSP 375: JSP 375 - Management of Health and Safety in Defence.

            1. JSP 515: JSP 515 - MOD Hazardous Stores Information Systems.

            1. MOD Form 640 - Advice and Inspection Note

NATO Documents

            1. STANAG 7175 - Definition of Safety Zones and Minimum Separation Distances for Use With Liquid Oxygen (LOx).

# 13 - Aviation Gases

Chapter Sponsor - DES AS AC- Airfield Eng 1

## Scope

            1. This chapter discusses the gas, gas cylinders and associated equipment available in support of the military air environment. It differentiates between ground-use gas cylinders and those used in an airborne application.

## General

            1. Gas Specifications. The specification for any gas used within an aircraft is determined by the aircraft Design Organisation.

            1. The standard specification for breathing gases for aviation use in MOD aircraft is detailed in Defence Standard 68-284.

            1. The standard specification for gas for use in aircraft pneumatic systems in MOD aircraft is nitrogen to Defence Standard 58-96. RAF and civil aircraft use only nitrogen in their pneumatic systems. Nitrogen is also the choice of the vast majority of NATO countries.

            1. In the Fleet Air Arm (FAA) some older designs of aircraft can use either compressed air or nitrogen as a medium for charging their pneumatic systems, however, modern aircraft such as the Merlin use nitrogen only. Historically, the requirement to use compressed air was due to the ease with which compressed air could be produced on board ships. All FAA aircraft operating from shore bases, or from ships provided with a source of nitrogen, are to use nitrogen in their pneumatic systems where this is an approved medium by the aircraft Design Organisation.

            1. Compressed air provided from HM Ships systems are to comply with Defence Standard 68-284 or the latest version of BS-EN-12021 for CNBA, as mandated by the respective Equipment Sponsor. Further information is detailed in BR 2000 (89), Article 0204.

## Aviation Ground Supply Gas Cylinders

            1. Where practical, all aviation gas supplied in ground supply cylinders will be provided in 50 litre water capacity cylinders at a pressure of 300 bars. These are the standard cylinders fitted to the Mk 3 servicing trolleys.

            1. Mk 3 servicing trolleys. The Mk 3 servicing trolleys are approved aviation Ground Support Equipment. The procedure to be followed when changing cylinders is detailed in the equipment publication. Refer to Table 13.1 The Support Authority for this equipment is the AC PT (GSE1d)

Mk3 4-cylinder breathing air trolley

Table 13.1 - Equipment details
Item description	Publication	NSN
Mk 3 single- and four-cylinder Nitrogen Trolley	DAP 119F-2743-123 & 5F / DAP 119F-2744-123 & 5F	71GD/3655-99-1293318 / 71GD 3655-99-3468696
Mk 3 single- and four-cylinder Oxygen Trolley	DAP 119F-2743-123 & 5F / DAP 119F-2744-123 & 5F	71GD/3655-99-2121274 / 71GD/3655-99-2510525
Mk 3 single- and four-cylinder Breathing Air Trolley	DAP 119F-2743-123 & 5F / DAP 119F-2744-123 & 5F	71GD/3655-99-8090034 / 71GD/3655-99-3769019

      1. STANAG 7146. In order to comply with STANAG 7146, Assignment of NATO code numbers to gases used in aircraft cross-servicing, certain gases used by NATO armed forces in aircraft cross-servicing operations will be identified with additional information indicating the NATO code number and the NATO product description. These gases are identified in Defence Standard 81-24. This information may be included on the precautionary label or, alternatively, an additional label will be attached to the cylinder. The label displayed in Part 2, Chap 3, Annex D may be used.

      1. It is the filler of a gas cylinder who is responsible for correctly identifying the contents.

## Aviation Gas Cylinders with an Airborne Application

      1. A large variety of compressed gas cylinders and cylinder assemblies are utilised for airborne applications. They can be fitted as integral components in aircraft or missile systems, form part of independent safety systems such as life-rafts or ejection seats or be fitted as part of removable mission specific role equipment.

      1. All compressed gas cylinders and cylinder assemblies used in an airborne application are designed, maintained and handled to meet stringent airworthiness requirements. Because of this they will often be subject to different procedures than those applied to cylinders used solely in ground applications. Listed in paragraph 13 below are major sources of information that can provide guidance concerning the handling, storage, specifications and maintenance, lifing, marking and operation of airborne compressed gas cylinders and cylinder assemblies.

PSTASS (Passenger Short Term Air Supply System) cylinders for aircrew.

      1. The following are sources of information relating to airborne cylinders:

Generic policy	MAM-P (Manual of Airworthiness Maintenance – Processes).
Marking of cylinders	Defence Standard 81-24. Identification Marking of Transportable Receptacles, Compressed Gas
Oxygen Cylinders	The 107D series of Air Publications
Note: Generic information can be found in DAP107D-0001-1 and DAP 107D-0111-12; remaining publications are specific to particular equipment.
CO2 and Air Cylinders used in life-rafts	The 108E series of Air Publications
Note: Generic information can be found in AP108E-0030-123, remaining publications are specific to particular equipment.
United States DoT Cylinders	Code of Federal Regulations Title 49
Cylinders supported by the / AP107A-0101-2(N/A/R)1, Airborne Aircraft Support PT (AC PT)	AP107A-0101-2(N/A/R)1, Airborne Gaseous Components - Support Authority General Orders & Special Instructions (Technical)

## Bibliography

            1. STANAG 7146 - Assignment of NATO code numbers to gases used in aircraft cross‑servicing.

            1. Defence Standard 58-96 - Pure Gases for Weapons Systems and Detector Cooling Applications.

            1. Defence Standard 68-284 - Compressed Breathing Gases for Aircraft, Diving and Marine Life-Support Applications.

            1. Defence Standard 81-24 - Identification Marking of Transportable Receptacles, Compressed Gas.

            1. MAM-P (Manual of Airworthiness Maintenance – Processes.

            1. BR 2000(89) – Compressed Gas System Design and Engineering Practice.

# 14 - Refrigerant and Fluorinated Gases (F Gases)

Sponsor - DSFA Technical Gases Manager

## Scope

            1. This chapter provides information on fluorinated gases (F-gases). F-gases are man-made gases comprising families of gases known as Hydrofluorocarbons (HFCs), perfluorocarbons (PFCs), sulphur hexafluoride (SF6) and Nitrogen Trifluoride (NF3). The most common F-gases are HFCs which generally referred to as refrigerant gases because they are used in applications such as refrigeration, air conditioning, and heat pump equipment.

## EU, UK and MOD Policy

            1. Introduction. There is detailed information on refrigerant gases and ‘F’- gases, the Montreal Protocol, the Kyoto Protocol, associated European and UK Legislation and the MODs Climate Change Strategy and general policy for the use and control of these gases within JSP 418, Vol 2. In particular:

Leaflet 6 - Fluorinated Gases (F Gas)

Leaflet 7 – Ozone Depleting Substances (ODS)

            1. All persons handling or using refrigerant gases and F-gases are to be fully aware of the MOD policy for using these products and are to ensure they comply with their responsibilities.

            1. All users of refrigerants and F-gases must:

Be trained to a recognised, accredited national standard as detailed in JSP 418 Vol 2, Leaflet 6.

Recover any controlled substance during maintenance and/or decommissioning of equipment.

Minimise leakages and avoidable emissions of the controlled substances from equipment.

            1. Deliberate venting to atmosphere of a controlled substance is illegal.

            1. Any waste material shall be disposed of in an approved manner. Team LEIDOS Lubricants and Gases Team can provide advice on the environmentally-safe disposal of refrigerants and sulphur hexafluoride and are able to dispose of them via their contractors.

            1. In accordance with JSP 418, Vol 2, Leaflet 6, all refrigerants that are recovered during maintenance procedures or from decommissioned or converted systems shall be offered, in the first instance to Team LEIDOS Lubricants and Gases Team, for recycling and possible use in support of MOD essential uses. Under no circumstances shall a contractor be allowed to take the refrigerants, unless they are to be used by that contractor in support of other MOD essential uses.

            1. The Hazardous Waste Regulations. The government has introduced regulations controlling the disposal of hazardous waste. Unwanted refrigerant gases and sulphur hexafluoride are classified as hazardous waste and the correct procedure for the disposal of hazardous waste is to be followed and the necessary documentation completed Refer to JSP 418 Volume 2 Leaflet 3 for the MOD policy on waste.

            1. The procedures to be followed for demand and return of recovered refrigerant gases and the required forms to be completed can be found on the JSP 319 defnet homepage.

            1. Refrigerant “User” The UK Government has introduced mandatory qualifications for users of Ozone Depleting Substances and other fluorinated gases (e.g. refrigerants, SF6) within the scope of the ‘F’ Gas Regulations. Refer to JSP 418 Vol 2 Leaflet 6, tables 2 and 3; leaflet 7 table 5, for list of applicable mandated Refrigerant user qualifications.

            1. The regulations specify minimum qualifications for personnel working with refrigerants and halons, and its recycling, reclamation or destruction. All MOD personnel and all MOD contractors who are required to work with refrigerants are to hold the requisite qualification.

            1. EU Regulation 517 / 2014 mandates the requirement of the ‘Seller’ of F-Gas to ensure that organisations they are supplying to are a competent body i.e. that they are meeting the existing legal training requirement. The requirement on the “User” to be a competent body is not new but placing a legal responsibility on the supplier to ensure they only supply to a competent body is new. A list of authorised users is found in the Letter of Assurance related to purchase of fluorinated greenhouse gases can be found in JSP 319 defnet homepage.

            1. The latest EU Regulations make it illegal for a “Seller” to sell F-gases to a “User” without evidence from the “User” that they are competent.

## Refrigerants and Refrigerant Cylinders

            1. Refrigerant gases have been classified as a Hazardous Substance. Unwanted refrigerant gases are categorised as Hazardous Waste and shall be returned using the appropriate recovery cylinder.

            1. All holdings and uses of f-gases have to be reported annually to DES TECH-QSEP HAZMAT via the respective TLB CESO. Losses are to be investigated and prevented, and where necessary reported to DES TECH-QSEP HAZMAT.

            1. Disposable cylinders. Refrigerants are not provided for MOD use in disposable cylinders. Disposable refrigerant cylinders shall not be used by MOD personnel or their contractors. Only reusable cylinders shall be used, where the cylinder can be returned to the supplier and any excess product recovered or disposed.

            1. Tropical fill. All refrigerant cylinders, supplied from the Team LEIDOS Lubricants and Gases Team , are provided at a standard suitable for use in a tropical environment (refer to Part 2, Chap 5 (cylinder filling) and Part 2, Chap 9 (cylinder storage).

            1. Safety Data Sheets. Safety Data Sheets are available for all refrigerant gases. See MTSR, HSIS, or look on the MOD Contractor website.

            1. Identifying common refrigerants. The refrigerant can be identified by:

Looking at the contents label.

Looking at the information stamped on the cylinder data plate.

            1. It should be noted that the colour schemes applied to refrigerant cylinders differ between the various gas supply companies. Details of the colour scheme used by the current MOD Contractor are published on the Contractor website.

            1. Pressure Temperature Relationship Chart. Pressure Temperature Relationship charts are available for all the refrigerant gases supplied to the military. An electronic version is published on the MOD Contractor website.

            1. Determining cylinder contents by weight. To determine accurately the cylinder contents at any given time, deduct the empty weight from the weighed weight. The empty weight is defined as the 'Tare Weight'. This will be stamped on the cylinder data plate. The weighed weight is known as the 'Gross Weight' and is a combination of the cylinder and its contents. The contents are known as the 'Net' weight.

  1. To calculate: Net Weight = Gross Weight - Tare Weight

            1. Filling capacity. The maximum permissible contents of a cylinder is stamped on its data plate. The figure will be variable depending on the density of the refrigerant. Typically, the maximum fill weight is approximately 80% of the cylinder’s total capacity in order to allow for thermal expansion.

            1. The maximum gross weight of a cylinder should never exceed the combined maximum fill weight (net) plus the tare weight.

  1. Maximum Gross Weight = Tare Weight + Max fill weight (Net).

            1. Management of cylinders. Refrigerants and sulphur hexafluoride cylinders need to be actively managed to ensure that cylinders do not leak, to detect leaks and to minimise the consequences of any leak. Cylinder management requires written procedures and record keeping for detecting and dealing with such problems (refer to Part 2, Chap 10) Weighing of cylinders on calibrated instruments is one technique detecting losses; other techniques include electronic or electrical devices and warning alarms.

## Bulk Storage of Refrigerants

            1. All bulk storage tanks and their associated pipe-work and protective devices are classed as pressure systems and shall comply with the Pressure Systems Safety Regulations, 2000; there are certain exceptions, but most if not all such systems in used for storing refrigerants will be subject to these regulations. JSP 375, Part 2, Vol 1, Chap 29 refers. Reference is also to be made to JSP 375, Part 2 Vol 3.

            1. Bulk storage systems shall be actively managed to ensure that there are no leaks, to detect leaks and to minimise the consequences of any leak. This management requires written procedures and record keeping for detecting and dealing with such problems (refer to Part 2 Chap 10).

            1. The storage site is to follow similar requirements to that detailed within Part 2, Chap 9, for the storage of gas cylinders, for its location, design, security and signage.

            1. Each individual bulk storage tank shall be clearly labelled with its contents and its associated UN product identification number. The appropriate gas hazard diamond shall also be displayed (refer to Part 2, Chap 3). For example:

Refrigerant Gas	UN Number
R134a	UN 3159
R404a	UN 3337

            1. The connection fittings of multi-storage installations, pipework connecting storage tanks to equipment or long fill lines shall be clearly marked with the gas name or symbol. Identification marking of pipelines shall comply with BS 1710.

            1. All displayed safety signs and warning notices shall be kept legible, visible and up to date at all times.

## Recovery Cylinders

            1. Cylinders. Team LEIDOS Lubricants and Gases Team provide a range of recovery cylinders to enable refrigerant and sulphur hexafluoride (SF6) to be returned to the contractor for either recycling or disposal (refer to Table 14.1).

Recovery Cylinder and R134a Cylinder

            1. Details of the refrigerants that may be recovered into a recovery cylinder are listed on the body label attached to the cylinder wall, or with a label attached to the collar, along with the maximum fill limit for each refrigerant. Refer to JSP 319 defnet homepage for all recovery cylinder labels.

            1. The maximum fill limit is a safe 'de-rated' weight for the cylinder specifically for a particular refrigerant. This is typically 25% of the normal virgin refrigerant maximum fill limit.

            1. If you have a refrigerant which is not listed on the body label of the the recovery cylinder, contact Team LEIDOS Lubricants and Gases Team for further advice.

WARNING: Not all recovery cylinders are suitable for all refrigerants. The correct recovery cylinder for a particular refrigerant is to be correctly identified.

WARNING: Do not use the recovery cylinder to recover F-gases unless you have explicit approval from Team LEIDOS.

            1. For the sulphur hexafluoride recovery cylinder, the maximum permissible fill, 43kg, is stencilled on the cylinder.

            1. In accordance with the current F Gas Regulations, the filler (the “User”) of a recovery cylinder shall be responsible for ensuring that:

  1. The cylinder is suitable for the refrigerant or sulphur hexafluoride being recovered.

  1. The contents are correctly identified.

  1. The cylinder is not over-filled.

  1. The information on the label is complied with and all relevant details are completed.

            1. Recovery cylinders shall only be filled when they are in date of their Periodic Inspection and Test (refer to Part 2, Chap 5).

            1. Refrigerants shall not be mixed in refrigerant recovery cylinders, and sulphur hexafluoride recovery cylinders are for sulphur hexafluoride (SF6) only.

            1. MOD users are not to convert virgin refrigerant supply cylinders into recovery / decant cylinders.

            1. To ease identification, refrigerant recovery cylinders will have a yellow band painted around the cylinder with the word "RECOVERY" or "RECOVERED REFRIGERANT" stencilled in 50mm black letters.

            1. All refrigerant recovery cylinders supplied by Team LEIDOS Lubricants and Gases Team are suitable for use in the decant role. They are provided with an appropriate level of internal cleanliness. These cylinders are vacuumed when returned to the contractor to ensure they are empty of gas then processed through a test shop where they are:

  1. Externally inspected.

  1. De-valved.

  1. Internally inspected (visually).

  1. Internally steam cleaned.

  1. Internally dried.

  1. Re-valved.

  1. Re-painted (if necessary).

            1. When used in the recovery role, refrigerant is to be recovered into the cylinder and then returned to the Team LEIDOS Lubricants and Gases contractor.

            1. When used in the decant role, recovery cylinders may be used to recover F-gas from applicable systems, i.e., refrigeration units, chillers, heat exchangers & etc, this is typically to allow maintenance to be carried out on the system. This refrigerant is then recycled (returned) back into the original system. It is not unusual for this refrigerant to contain traces of oils and other contaminants. The user is responsible for ensuring the quality and quantity of any refrigerant returned into a system.

            1. Refrigerant recovery cylinders may be used in either to decant, or the recovery role. However, once used in the recovery role, cylinders should not subsequently be used in the decant role and once used in the decant role, cylinders should be used only for the refrigerant decanted in the recovery role.

            1. Overfilled recovery cylinders. It is unsafe to overfill recovery cylinders. Under the Environmental Protection Act (EPA 1990) all producers of waste refrigerant have a duty of care to ensure:

Waste is properly identified on waste transfer documentation. In this context, the correct weight of the recovered refrigerant gas shall be annotated on the label affixed to the cylinder neck / body as appropriate.

Waste is despatched to certified parties

Waste packages are safe to be transported.

            1. It is the responsibility of the “User” / person carrying out the maintenance activity to correctly record the refrigerant gas type and weight on the recovery cylinder label. Gas cylinder store managers shall only accept filled recovery cylinders if the label / table on the recovery cylinder have been correctly completed by the “User”. Checks by the gas cylinder store manager shall include:

  1. Only 1 type of refrigerant has been entered into the recovery cylinder.

  1. The weight of contents has been recorded.

  1. The recorded weight of refrigerant does not exceed the corresponding weight annotated on the table affixed to the recovery cylinder body.

            1. The risks from overfilling a recovery cylinder are:

  1. Possible cylinder rupture during transport and storage.

  1. Increased risk when handling cylinders, with a potential risk of injury to personnel.

  1. Damage to the cylinder which will require the cylinder to be scrapped (weakening of the cylinder wall).

            1. If a cylinder has been overfilled contact Team Libidos Lubricants and Gases Team for further advice. Where cylinders have been overfilled and returned through the supply chain without the knowledge of Team LEIDOS Lubricants and Gases Team or their contractor, apart from the risk of failure and subsequent risk of injury to personnel, the filler would be in breach of legislation and may be liable for any costs for the replacement of that cylinder.

            1. Return of Recovery Cylinders. Virgin refrigerants in opened/part full cylinders, recovered refrigerants in recovery cylinders, virgin sulphur hexafluoride in opened/part full cylinders and recovered sulphur hexafluoride in recovery cylinders shall be returned in accordance with the current hazardous waste regulations.

            1. Unused Recovery cylinders (i.e., Cylinders that are supplied empty by the Contractor) are fitted with “shrink wrap” around the valve. Any Recovery Cylinder that has the “shrink wrap” removed is to be considered as used and shall be subject to the caveats in this Chapter for return.

            1. As recovered refrigerants and recovered sulphur hexafluoride may be contaminated with oils, water, trace acids, or other breakdown products, used recovery cylinders should be returned promptly to minimise the effects of corrosion on the cylinder walls. They must also be returned whilst they are within their Periodic Inspection and Test Date.

            1. Details of Recovery cylinders. Refer to MOD/ Contractor’s website.

Table 14.1 - Recovery Cylinders
NSN / Contractor’s Product Code No.	Water Capacity (litres)	Suitable for:
71C/0443 8120-99-8525944. / 333102-RKZ	61	Halon 1211, R12, R114, R22, R134a, R236fa, R245fa, R401A, R403B, R404A, R407C, R409A, R410A, R413A, R417A
71C/0443 8120-99-5516582. / 333103-RAZ	11.34	Halon 1211, R12, R114, R22, R134a, R236fa, R245fa, R401A, R403B, R404A, R407C, R409A, R410A, R413A, R417A
71C/O443 6830-99-6665358. / P158964-R60	57.5	R134a+UV
71C/O443 8120-99-9120280. / 160392-RJ	47.2	Halon 1211, Halon 1301, R12, R114, R22, R134a R407C, R236fa, R245fa, R401A, R403B, R404A, R409A, R410A, R413A and R417A
71C/O443 8120-99-7367462. / 160383-RF	9.4	Halon 1211, Halon 1301, R12, R114, R22, R134a R407C, R236fa, R245fa, R401A, R403B, R404A, R409A, R410A, R413A and R417A
71C/O443 8120-99-2508963. / 161079 RJ	47.2	Sulphur hexafluoride (SF6)

## Bibliography

      1. JSP 418: JSP 418 - Management of Environmental Protection in Defence.

      1. JSP 515: JSP 515 - MOD Hazardous Stores Information System.

      1. DIN 2005DIN07-004: DIN 2005DIN07-004: New Hazardous Waste Regulations.

      1. Environmental Protection Act 1990: UK Public General Acts1990 c. 43, Environmental Protection Act 1990).

      1. Hazardous Waste Regulations: UK Statutory Instruments2016 No. 336, The Hazardous Waste (England and Wales) (Amendment) Regulations 2016.

      1. Special Waste Amendment: Scottish Statutory Instruments2004 No. 112, The Special Waste Amendment (Scotland) Regulations 2004.

      1. Ozone Depleting Substances Regulations: UK Statutory Instruments2015 No. 168, The Ozone-Depleting Substances Regulations 2015.

      1. Montreal Protocol: The Montreal Protocol on Substances that Deplete the Ozone Layer, UN Environment Programme, Ozone Secretariat.

      1. Kyoto Protocol: Kyoto Protocol to the United Nations Framework Convention on Climate Change, Kyoto, 11 December.

      1. The Fluorinated Greenhouse Gases Regulations 2021: UK Statutory Instruments2021 No. 543, The Fluorinated Greenhouse Gases (Amendment) (EU Exit) Regulations 2021.

      1. BS 1710 - Specification for Identification of Pipelines and Services.

# 15 - Medical Gases

Chapter Sponsor - DES LSOC-CMO-Ops-Comply-RP

## General

            1. Physically medical gases are similar to other non-medical gases; however, they are prescribed and/or administered to patients by a healthcare professional. Under the Medicines Act 1968,Human Medicines Regulations 2012 and The Human Medicines (Amendment) (EU Exit) Regulations 2021 medical gases are classified as medicinal products and have to meet the specification detailed in the appropriate UK and/or European Pharmacopoeia. Only these approved medical gases are to be used for medical purposes. Like other medicinal products they need to have a Marketing Authorisation (product licence) in order to be supplied. The Marketing Authorisation defines when a gas can be used and how it should be administered to a patient. Only medical gases with an appropriate licence should be prescribed for the treatment of patients.

Note: Medical gases and medical vacuum systems are not to be used for non-medical purposes, other than a power source for medical equipment or for testing medical equipment.

Further information on medical gases can be obtained from HQ Defence Medical Services, the sponsor or Team LEIDOS. JSP 950 Leaflet 9-2-1 details the MOD medical policy and legislation behind the use of medicinal products.

The supply of medical gases is provided by the current MOD gas supply contractor, which is managed by Team LEIDOS.

Medical gases supplied by authorised MOD contractors meet the specifications detailed in the European Pharmacopoeia. When demanding medical gases, units will only receive those medical gases supplied by authorised MOD contracted suppliers. No other medical gas cylinders from unauthorised MOD suppliers should be procured and administered to patients by UK Force Elements. This does not apply to any oxygen administered in an emergency by the Host Nation. Locally sourced medical oxygen, procured in anticipation of administration in an emergency, (e.g. for Diving AT) should conform to European Pharmacopoeia standards. A Certificate of Conformity must be obtained to evidence compliance with this standard. Medical oxygen that is not compliant with European Pharmacopoeia standards may be procured and used in extremis on the authority of the Competent Medical Authority, who will formally assess and document the risk

Empty cylinders should not be retained for longer than necessary, but returned at the earliest opportunity to the supplier to avoid unnecessary rental charges. Backloading follows the same rules as any other commodity. Empty cylinders can be held at Bicester or Donnington before they are returned to BOC. Full cylinders are only to be held at B56 in MOD Donnington.

Team LEIDOS are the Technical Authority for medical gas cylinders and their associated valves, guards, etc.

## Medical Gases, and Gas Cylinder Properties

Medical gases have a life of three years from the date of filling. The expiry date will be indicated on the contents label. Once this life has expired, the gas cylinder is to be returned and replaced with a serviceable item. In addition, each cylinder is given an initial inspection and test at the time of manufacture, a pre-fill inspection is carried out prior to each fill and a periodic inspection and test is carried out at set frequencies or when the pre-fill inspection determines a need. Medical users must ensure that the cylinder is within its expiry date. NOTE: Cylinders will only be filled and transported if they are in date for their periodic inspection and test, however, you are allowed to transport an out-of-date cylinder provided you are returning it to a place where it will be tested.

A transportable gas cylinder past its Periodic Inspection and Test date may continue in use at a static location (subject to its serviceability and any independent life on the gas contents). On expiry of their Periodic Inspection and Test life transportable gas cylinders may be transported only for purposes of returning them back to a place where the Periodic Inspection and Test will be carried out (return to the supplier/contractor). Cylinders do not have to be empty when transporting, the majority are not. As long as there is no obvious defect with the cylinder / valve it can be transported.

It is recommended that all cylinders which have passed their periodic inspection and test date are returned to the gas cylinder supplier and, as required, replaced with serviceable items, iaw Defence Logistic Framework (DLF). Refer to JSP 319 Pt 2 Vol 1 Chap 7 Paras 13 & 14, Chap 8 Para 14 and Chapter 4, JSP 375 for details.

Expired medical gas shall be considered the same as any other expired drug. The medical gas is expired when it has gone beyond the gas life specified on the cylinder. An expired medical gas may be operationally extended, like other consumable medications, in extremis, after taking advice from the medical Chain of Command.

Liquid medical oxygen does not have an expiry date.

Entonox™. Nitrous oxide begins to separate out from Entonox™ if the temperature falls below about -6°C. A homogeneous mixture is again obtained when the temperature is raised to above +10°C and the cylinder agitated. Before use, to ensure it is properly mixed, cylinders should be stored horizontally for 24 hours at a temperature above +10°C. If cylinders are stored at temperatures lower than 0°C for long periods before use, they should be warmed above 10°C for three hours and then inverted at least three times to ensure homogeneous mix. Under no circumstances should cylinders be immersed in water before use. Detailed information is available on the Safety Data Sheet.

The production of medical oxygen requires specific authorisation and licences from the MHRA. Service units shall not manufacture medical gases for medical purposes without the appropriate authorisation of SO1 Pharm HQ DMS Gp SG-DMed-Med-Pol-GpMailbox@mod.gov.uk AND the DE&S Defence Responsible Person.

All Medical Gas cylinders have been cleared for use in the Forward Edge Battle Area but may only be carried in the Forward Edge Battle Area when the increased “Battlefield” level of risk of not providing medical gas outweighs the increase in “Platform” risk of carrying the medical gases.

WARNING: Testing has shown that penetration by 7.62mm ammunition causes explosive rupture of this type of cylinder.

Where medical gases are to be sent to tropical climates via sea/air transport, there is a requirement to ensure that they are dispatched in accordance with Part 2, Chapter 3, para 25.

## Contaminated Medical Gas Cylinders

When being used in the medical environment, there is the potential for medical cylinders to become contaminated. Whilst blood and body fluids may be visible, there is also a risk of non-visible contamination. This could lead to the risk of transfer of viruses and bacteria. Suspected cylinders should be wiped down with a clean damp cloth as outlined in HTM 02-01 Part B para 131 Safety notes.

a.	For UK Firm Base, any cylinders contaminated with bodily fluids should be quarantined from further use, washed with warm water, allowed to dry and then placed in a “contaminated cylinder bag” for return to supplier. Contaminated cylinder bags are available free from BOC. Further information is available here.

For Overseas Firm base and Operations, cylinders contaminated with bodily fluids, should be cleaned with a detergent wipe (e.g. Sani Cloth detergent wipe NSN 8508-99-772-6594). For specific disease or blood contamination - soak-up any excess bodily fluid with blue roll, decontaminate area with Clinell Wipes (NSN 7930-99-581-9376.

Any contamination of the valve or regulator area should be treated as gross contamination and cylinder marked accordingly and quarantined from further use. An individual risk assessment with IPC specialist (including reachback if necessary) should be conducted and documented (Discussion with manufacturer may be necessary).

WARNING: MOD personnel shall not use chemicals to assist in the cleaning process
as these may have a detrimental effect on the cylinder or its gas. As required, seek
advice from Team LEIDOS or the gas cylinder supplier.

For further advice contact Infection Prevention Control IPC) Reach back Service. Gross contamination is rare, but in this event, IPC reach back should be contacted for advice, as certain chemicals can cause degradation of cylinders. Further guidance is also available from the British Compressed Gases Association.

If there is any doubt with regard to the hygiene condition of medical gas cylinders, the store manager / DG shipper shall not handle medical gas cylinders and seek medical advice immediately.

## Storage of Medical Gas Cylinders

As well as complying with JSP 319, Part 2, Chapter 9, The only licensed premises within MOD for depot storage is B56 in MOD Donnington. Full or partially full medical gases are not to be stored within any other depot.

General storage principles are:

        1. Cylinder stores for medical gases should only contain medical gas cylinders.

        1. Separate, clearly identified bays should be provided for full and empty cylinders.

        1. Separate areas for different gases should be provided, but it is not necessary to construct a physical barrier unless it is convenient to do so.

        1. Clear and secure access to all cylinder stores is required, including adequate space for vehicular access and cylinder loading/unloading.

        1. The floor of the store should be level or constructed of concrete, or non-combustible, non-porous materiel.

        1. Gases should be stored securely to prevent any tampering.

        1. All cylinder stores should be covered and ventilated. When constructed of brick or other solid material, ventilated by means of high- and low-level vents.

        1. The location of the cylinder store should be marked clearly on the site plan for ease of identification in the event of an emergency.

        1. Adequate means of securing large cylinders should be provided to prevent falling.

        1. Smoking and naked lights should be prohibited in the vicinity of all cylinders.

        1. Appropriate safety signage should be provided in all cylinder stores in accordance with HTM 02-1, Part B, Chap 14.

        1. This is not exhaustive and Further detail can be found in HTM 02-01, Part B, Chap 8.

        1. Ensure that the storage temperature does not exceed 52°C (125°F) and is ideally above 10 degrees. Store, handle and use compressed gas cylinders securely fastened in place in the upright position. Never roll, drag, or drop cylinders or permit them to strike each other. Type E gas cylinders are being not exceed 34°C (93°F) since the relief valves of Type E cylinders are set to release above 35°C.

Operations / Exercises. Where practicable, storage of all gases on operations / exercises shall be as for non-operational storage. Those elements that cannot be achieved without compromising operational effectiveness may instead be risk assessed (see and the risks mitigated as far as possible by the Delivery Duty Holder (DDH), with the risks entered on the corporate risk register. Only when assessing the risk in an operational theatre, may the risk to operational effectiveness be given higher priority to the risk of life; when this is done, the operational commander (DDH/ ODH) shall give explicit authorisation. Further guidance can be found at Part 2, Chapter 18 Para 101 - 109.

## Bibliography

NHS Protect Document - Guidance on the security and storage of medical gas cylinders:

HTM 02-01 - Medical gases, Health Technical Memorandum 02-01: Medical gas pipeline systems: Part A: Design, installation, validation and verification.

HTM 02-01 - Medical gas pipeline systems, Part B: Operational management.

JSP 950 - Medical Policies.

# 16 - Diving Gases

Chapter Sponsor – Defence Diving Standards Team (DDST) – Superintendent of Defence Diving

## Scope

This chapter provides information on gases and associated gas cylinders used by those engaged in Defence diving activities, where the gas cylinders are provided to replenish MOD dive sets. It does not cover diving cylinders that are used underwater.

Defence diving activities include the RN, Army, MAB, MOD civilian divers and MOD Adventurous Training (AT) diving activities.

## General

The use of diving gases and diving gas mixtures is strictly controlled by written instructions and procedures; information and guidance is available in:

JSP 286: Defence Diving Manual - Part 1.

JSP 286 Pt 2: Guidance - Vol 1 – 8.

BRd 2807 Series. (Equipment Handbooks).

CNBA procured for MOD diving applications comply with Defence Standard 68-284 or the latest version of BS EN 12021 as mandated by the responsible Operating Authority and applicable Equipment Sponsors respectively. A Certificate of Conformity to the required specification will be supplied by the MOD contractor with all deliveries of gas cylinders and MCPs. Within NATO, military diving gas has to be compliant with STANAG 1458. STANAG 1458 is implemented in the UK via Defence Standard 68-284. The specification and testing requirements for diving gases is detailed in Part 2, Chap 6.

In the event of a gas being supplied by the MOD contractor which does not meet the required specification DSFA Technical Gases Manager shall be informed.

All diving gases have a life expiry date, beyond which they are NOT to be used. Typically, this is 5 years from the date of fill. The MOD contractor shall affix a label on each cylinder / MCP it delivers with its expiry date.

Team LEIDOS Lubricants and Gases Team supplied cylinders and MCPs are NOT authorised for use underwater.

Where cylinders are used in a salt water environment, all reasonable precautions are to be taken to prevent contact with salt water. In the event of salt water contact then the cylinder is to be thoroughly washed down with fresh water at the earliest opportunity. If the user believes that, for whatever reason, water may have entered the cylinder, the cylinder is to be declared unserviceable and returned.

Divers may operate in explosive and magnetic sensitive areas; it is standard practice to provide gas cylinders, and their associated components, that are manufactured from non- low magnetic materials.

MOD divers are specifically authorised to re-fill Team LEIDOS Lubricants and Gases Team supplied compressed air cylinders. To meet this requirement the standard Pressure Retention Valves are removed from compressed air cylinders. Oxygen and mixed gas cylinders are NOT to be refilled by anyone other than the Team LEIDOS Lubricants and Gases Team contractor. For filling procedures and authorisations refer to Part 2, Chap 5.

Compressed air cylinders are only to be refilled when in date for their Periodic Inspection & Test. If out-of-date then the cylinder is to be replaced. The test life is 5 years.

The filler is responsible for ensuring the correct specification and quality of the gas.

Manifolded Cylinder Packs (MCP- “Bundles”). Team LEIDOS Lubricants and Gases Team provide the following two types of MCP from the MOD gas supply contract:

              1. 'WL' MCPs which consist of 15 cylinders, stored vertically, manifolded together and contained within a frame. These are designed for use within the UK and meet the requirements for the transportation of dangerous goods by road (DSA03.DLSR, Movement and Transport Safety Regulations – Dangerous Goods Manual). These are the preferred MCPs for use in the UK.

              1. 'ELD' MCPs which consist of 16 cylinders, stored vertically, manifolded together and contained within a frame. These are more robust than the 'WL' MCPs and are designed for use world-wide. They meet all the requirements for the transportation of cleared for transportation on military transport aircraft (DSA03.DLSR, Movement and Transport Safety Regulations – Dangerous Goods Manual). This MCP has also been cleared for carriage as a helicopter underslung load, DAP101A-1105-1B, helicopter underslung load clearance No. 7006 refers. As these are more expensive to supply it is recommended that their use is restricted to areas outside of the UK.

## Quality Assurance

Checking contents of breathing gases. Although gas supply companies are rigorous in controlling diving breathing gases, experience has shown that it is possible for a gas to be supplied which does not correspond to the cylinder marking.

All diving gas cylinders are to be checked, using an in-service analyser, upon receipt and re-checked prior to connecting them to a diving gas supply or breathing apparatus charging system. Each check is to ensure that:

Gas cylinder “Receipt and Issue” checks are carried out, refer to Part 2, Chap 10.

The precautionary label correctly identifies the gas contents; refer to Part 2, Chap 3.

The gas is compliant with current in-service standards, and is the correct gas for the system it is to be used in.

The colour code aligns with the contents of the cylinder, refer to Part 2, Chap 3.

The Certificate of Conformity is present and aligns with the contents of the cylinder.

The gas is in-date for use.

The cylinder is in date for its Inspection and Test, refer to Part 2,Chap 3.

The serial number of the cylinder is highlighted.

These checks are to be carried out by a competent person when the gas is delivered to the storage area and again by the person conducting the charging of diving equipment or fitting to a re-compression chamber prior to use.

Additional testing is required as laid down in the references in para 3 (above) and HSE Diving Information Sheet No 9 – Breathing Gas Standards and the Frequency and Examination and tests. All diving gases are to be analysed on receipt using an in-service analyser as detailed in Part 2, Chap 6, and/or other test equipment approved for use by the responsible Equipment Sponsor. Once analysed this is to be noted on the Certificate of Conformity with the date and name of the person who conducted the check.

Identification of diving gases. All cylinders and MCPs containing diving gases are to be identified in accordance with Part 2, Chap 3, additionally the following information shall also be shown:

Where the gas is a mixture, the percentage by volume, quoting the percentage of oxygen first.

To assist in the identification of individual cylinders and their maintenance history the following details are highlighted on all cylinders supplying diving quality gas:

Serial number of the cylinder.

The most recent (periodic) inspection and test date.

Quality assurance of compressed natural breathing air. Where compressed natural breathing air is produced on-site comply with the quality testing requirements detailed in Part 2, Chap 6.

## Handling and Use

The range of contractor supplied diving gas 20 litre cylinders are fitted with a valve guard. This valve guard has been designed and manufactured to allow a cylinder to be lifted either manually or by slinging.

The gas cylinder supplier will ensure the valve guard is secure and serviceable on delivery. However, it is good practice to ensure that the guard is securely attached and that there are no obvious signs of damage before attempting to lift or sling the cylinder.

## Bibliography

JSP 286 Defence Diving Manual Part 1.

JSP 286 Pt 2: Guidance - Vol 1 - 8

BRd 2807 Series (Equipment Handbooks).

JSP 375: JSP 375 - MOD Health and Safety Handbook.

DSA03.DLSR, Movement and Transport Safety Regulations – Dangerous Goods Manual.

DAP101A-1105-1B: DAP101A-1105-1B - Underslung Load Clearances.

Defence Standard 68-284 - Compressed Breathing Gases for Aircraft, Diving a Marine Life-Support Applications.

STANAG 1458 - Diving Gas Quality.

ADR - Agreement concerning the International Carriage of Dangerous Goods by Road

IMDG - The International Maritime Dangerous Goods Code.

International Marine Contractors Association (IMCA) D 043, Marking and colour coding of gas cylinders, Quads and Banks for Diving Application.

# Chapter 17- Introduction to LPG

Chapter Sponsor - DIO TS Eng Gas AH

## Scope

            1. Liquefied Petroleum Gas (LPG) is used in bulk by the MOD for heating of premises, including field accommodation; for cooking; and in Automotive Mechanical Transport Fuelling Installations (MTFI) for dispensing LPG to vehicles. Typically, the bulk storage system will be designed, installed, commissioned and filled/re-filled by a LPG contractor.

            1. Defence Logistic Framework (DLF) details the procedures for demanding LPG for the replenishment of bulk tanks. Further queries can be directed to (DIO TS-Eng Gas AH) Jeremy.Obbard100@mod.gov.uk

## Defence Infrastructure Organisation (DIO)

            1. Permanent infrastructure on the MOD estate is the responsibility of DIO. The MOD focal point for permanent infrastructure within DIO is:

Defence Infrastructure Organisation - Technical Services
DIO HQ, St George’s House,
DMS Whittington,
Lichfield,
Staffordshire,
WS14 9PY

Email: (DIO TS-Eng Gas AH) Jeremy.Obbard100@mod.gov.uk

The main safety framework is described in JSP-375- Vol 3.

LPG networks fall outside of the scope of the Gas Safety (Management) Regulations. However, they must be accommodated within an appropriate equivalent management system. The specific criteria required to adequately manage the operation of LPG network is described in: -

  1. Health and Safety at Work Act 1974.

  1. Management of Health and Safety at Work Regulations 1999.

  1. Pipelines Safety Regulations 1996.

  1. LPG Industry Codes of Practice.

JSP 375 Vol 3 Chapter 8 (Gas) and the DIO produced Gas Safety Management Plan (GSMP) Section A or C, as applicable, provides site-specific information ensuring the philosophy of the MOD/DIO Gas Safety Case can be effectively applied to the management of the LPG network across applicable MOD sites.

## Liquefied Petroleum Gas Trade Association

Liquid Gas UK is the voice of authority for the LPG and bioLPG industry in the UK. It was rebranded from UKLPG to diversify to bioLPG. It is the authoritative voice on LPG standards and its codes of practice are both globally recognised and industry leading. Several Codes of practice are referenced within this JSP:

Liquid Gas UK
Camden House
Warwick Road
Kenilworth
Warwickshire
CV8 1TH

Web: https://www.liquidgasuk.org/
Email: mail@liquidgasuk.org

## Safe Handling of LPG

Safe Handling of LPG. The types of liquid petroleum gases generally available within the UK are Commercial Propane and Commercial Butane. Everyone concerned with storage and handling of LPG are to make themselves familiar with the following characteristics and potential hazards.

Before using any hazardous substance or material, the user is to be conversant with the hazards and associated information detailed on the applicable SDS (MTSR, HSIS).

LPG is stored as a liquid under pressure. It is almost colourless, and its weight is approximately half that of an equivalent volume of water.

LPG vapour is denser then air, propane vapour is about 1.5 times heavier then air. Consequently, it may flow along the ground and into underground cable ducts, drains and gullies sinking to the lowest level of the surroundings and be ignited at distance from the source. In still air the vapour will disperse more slowly.

LPG can form a flammable mixture when mixed with air. The flammable range at ambient temperature and pressure extends between approximately 2% of the vapour in air at its lower limit and approximately 10% of the vapour in air at its upper limit (Note: For comparison, Natural gas has a flammable range of 5.0% to 13.5% in air). Within this range there is a risk of ignition. Outside this range any mixture is either too rich or too weak to propagate a flame. However over-rich mixtures can be hazardous when diluted with air. At pressures greater then atmospheric, the upper limit of flammability is increased but this increase with pressure is not linear.

Escape of even small amounts of LPG can give rise to large volumes of vapour/air mixture and thus cause a considerable hazard. A suitably calibrated explosimeter may be used for testing concentration of LPG in air. DO NOT use a flame for detecting leaks. Similarly, do not turn electrical equipment on or off, as a spark may be produced. Because of the potential to produce explosive atmospheres, (e.g. during bulk receipt of LPG), a DSEAR risk assessment shall be required in accordance with JSP 375, Vol 2, Chapter 9.

At very high concentrations in air, LPG vapour is an anaesthetic and consequently an asphyxiant, by diluting or decreasing the available oxygen. Therefore, if an LPG leak is suspected do not enter any Confined Spaces, basement areas, drains, or gullies, etc.

Commercial LPG is normally odorised before dilution by the addition of an odorant such as ethyl mercaptan or dimethyl sulphide, to enable detection by smell of the gas at concentrations down to one fifth of the lower limit.

Escape of LPG may be noticeable other than by smell. When the liquid evaporates, the cooling effect on the surrounding air causes condensation and even freezing of water vapour in the air. This effect may show itself as frost at the point of escape thus making detection easier. Leaks can also be identified due to shimmering in the air.

Because of the rapid vaporisation and consequent lowering of temperature, LPG can cause severe frost burns when in contact with the skin or the eyes. Personal Protective Equipment (PPE) is to be worn when handling LPG (see Part 2, Chap 2).

If an LPG cylinder or tank is exposed to flame above the liquid fuel line, it may rupture by boiling liquid expanding vapor explosion (BLEVE) causing violent release of the LPG, resulting in a fireball.

Competence of personnel maintaining LPG systems. The Gas Safety (Installation and Use) Regulations 1998 apply to the majority of vapour phase LPG installations. Only personnel registered with Gas Safe Register are permitted to carry out work on gas installations as defined in the regulations. Comply with JSP 375.

## LPG Medical First Aid

In all cases of injury from LPG qualified medical assistance is to be called immediately. All cases of injury through contact with LPG shall be given medical attention without delay.

All units who use, store or transport LPG are to have Standard Operating Procedures in place for dealing with cases of injury through contact with LPG. These are to be endorsed by the senior medical officer on the unit. The unit is to carry out a First Aid Assessment with emphasis on the hazard from LPG (see JSP 375). Any equipment identified in the First Aid Assessment is to be provided and maintained in a serviceable condition. Signage across the site is to clearly identify First Aid equipment locations and the nominated First Aiders.

LPG can cause the following problems:
Cold burns (frostbite) will result from skin/eye contact with liquid, prolonged contact can result in hypothermia.

Liquid release or vapour pressure jets present a risk of serious damage to the eyes.

Abuse involving wilful inhalation of very high concentrations of vapour, even for short periods can produce unconsciousness and might prove fatal. Inhalation may cause irritation to the nose and throat, headache, nausea, vomiting, dizziness and drowsiness. In poorly ventilated or confined spaces, unconsciousness or asphyxiation may result.

Skin Contact. Freeze burns may be caused when liquid LPG is in direct contact with exposed skin. The following First Aid is to be carried out:

Immerse affected area, or flush copiously, with tepid or clean cold water for at least 10 minutes to normalise temperature and until circulation returns. Do not expose area to hot water or direct heat.

Loosen any clothing that may restrict blood circulation to the affected area.

Thaw out frozen protective clothing, if it is NOT stuck to the skin remove it, avoid excessive heat. LPG vapour may be driven off during thawing.

Cover affected area with clean, dry, sterile dressing; bulk protective dressings should not be too tightly applied. Do not apply ointments or powders.

Alcoholic beverage and smoking is not to be permitted.

Inhalation. Remove the affected person to fresh air. Keep the patient warm and at rest. If breathing has stopped administer artificial respiration. Give external cardiac massage if necessary. If the person is breathing, but unconscious, place them in the recovery position.

Eyes. Cold burns should be flushed immediately with cold water for at least 15 minutes to normalise temperature. Hold eyelids apart while flushing to rinse entire surface of the eye and lids with water. Cover the eye with a sterile dressing.

## Safety Signs and Warning Notices

Appropriate and legible warning signs and pictograms shall be displayed and maintained in good condition in accordance with The Chemicals (Hazard Information and Packaging for Supply) (Amendment) Regulations 2008, The Carriage of Dangerous Goods (Classification, Packaging and Labelling) and Use of Transportable Pressure Receptacles Regulations 1996; and the Health and Safety (Safety Signs and Signals) Regulations 1996; BS EN ISO 7010:2020+A1:2020. All wording shall be in English. For installations located overseas there is a legal obligation to provide notices in the language relevant to the local civilian population and work force (operator).

Boundary warning signs and pictograms shall be clearly visible from all angles of approach, preferably sited with the centre of the sign at the average eye level (between 1.5 and 1.7 m above the ground). In exceptional cases, sites may be subject to the imposition of additional requirements by their local authority.

All LPG storage sites shall display the following signs/pictograms/notices on the access point and boundary fence or wall:

NO SMOKING.

NO NAKED LIGHTS.

NO STORAGE OF OIL, GREASE OR COMBUSTIBLE MATERIALS.

AUTHORISED PERSONS ONLY.

NO MOBILE PHONES.

NO STEEL TIPPED SHOES / BOOTS.

The Flammable gases transport Diamond Hazard Label.

LIQUEFIED PETROLEUM GAS or LPG

As an explosive atmosphere may exist, the Dangerous Substances and Explosive Atmospheres (DSEAR), requires that an Explosives Atmospheres sign be displayed (see Figure 17.1).

At the entrance to the site the appropriate fire signs and notices (e.g. Fire Action Notice) are to be displayed. A sign shall also be displayed detailing any specific action to be taken in the event of an incident / emergency and showing whom to contact in the event of an incident/emergency with all appropriate contact details. This is to include the unit emergency contact details and the contact details for the gas supplier and the gas supplier’s 24-hour emergency contact telephone number. The location of any access keys, as well as the contact details for the authorised key holder shall be displayed. Each individual bulk storage tank is to be clearly labelled with its contents and its associated UN product identification number. These are the proper shipping name and the UN number, e.g:

LPG	UN number
PROPANE	UN 1978
BUTANE	UN 1011

Figure 2.1.17.1 - Example of Warning Signs with Pictograms

LPG pipelines, Pressure Relief Valves and system shut-off and Emergency valves should be suitably labelled see LPG Industry Codes of Practice.

A sign is to be displayed at the LPG emergency shut-off valve, at the location, where it enters a building. The sign is to identify the valve as being the LPG Emergency Shut-Off Valve and it is to display the action required to shut-off the valve.

# 18 - Liquefied Petroleum Gas (Cylinders)

Chapter Sponsor - DIO TS Eng Gas AH

## Scope

      1. This chapter specifically covers Liquefied Petroleum Gas (LPG) Cylinders. Bulk LPG is covered in Part 2, Chapter 19.

      1. LPG cylinders are to be demanded/returned using the procedures detailed in Defence Logistic Framework (DLF).

      1. The LPG contract is owned and managed by DIO. Please note that Calor have been awarded the Cylinder contract for the whole of the GB (Excluding Northern Ireland). The Expire date of this contract is Feb 2026. The POC are:

Eaton, Mark Mr (DIO RD Util-Energy Supply Lead)
 Mark.Eaton655@mod.gov.uk

Martin, Kathryn D (DIO RD Util-Del Fuel Account Mgr)
 Kathryn.Martin131@mod.gov.uk

      1. Package Size. LPG may be measured by volume of liquid or weight. In cylinders it is measured by weight by deducting the empty tare weight of the cylinder from the total weight of the cylinder once filled.

LPG cylinders

      1. Portable receptacles. A portable LPG receptacle is defined as a receptacle with a capacity that does not exceed 150 litres of water, i.e. 150 litre Water Capacity. Portable receptacles are of two types:

Refillable. Referred to as cylinders these are fitted with a manually operated or automatic valve. Butane receptacles are normally 4.5, 7, 11.3 and 15 kg capacity, however the MOD does not have a contract for the 7 kg capacity cylinder therefore this cylinder is not to be ordered or procured. Propane receptacles are normally 3.9, 13, 19 and 47 kg capacity. Cylinders usually belong to the supplier and are exchanged on a one for one basis.

Expendable. Often referred to as cartridges, these receptacles are for once use only and will either be fitted with a pierceable disc or a self-sealing valve. The capacity of an expendable receptacles does not exceed 1.4 litre, i.e. 1.4 litre Water Capacity.

## LPG Cylinder Marking and Labelling

      1. The markings listed in the following paragraphs apply to LPG cylinders procured and used within the UK. Differing standards may apply in other countries and in such cases the information is to be sought from the organisation responsible for setting the contract.

      1. All LPG cylinders are to have their contents appropriately identified (refer to Part 2 Chap 3). Propane cylinders are normally coloured red and butane cylinders and cartridges are normally coloured blue. The markings applicable to butane and propane cylinders under these regulations are outlined in the Table 18.1. below.

Table 18.1 – Markings applicable to butane and propane cylinders
ITEM	BUTANE	PROPANE	REMARKS
Supplier	Name, Address & Telephone No	Name Address & Telephone No	See Note 1
Danger warning Symbol	Class 2.1	Class 2.1	See Note 2
Risk Phrase	Extremely Flammable	Extremely Flammable
Product Name	Butane	Propane
UN Number	1011	1978	See Note 3
Net Contents	xxx kg	xxx kg
Notes: / 1. To be sufficient for clear identification and contact. The telephone number is for information purposes only and does not need to be continuously manned. / 2. The symbol should be as large as practicable up to 100mm sides. It is to be clearly displayed on the cylinder (refer to Part 2, Chap 3). / 3. There are also other products e.g. unstenched LPG UN 1965 Hydrocarbon gas mixture N.O.S

      1. Cylinders will also display the following information:

Manufacturer’s mark and serial number.

Design code and year of manufacture.

Date of pressure test and test pressure (bar).

Minimum water capacity (litres).

Tare weight (kg).

      1. Marking of the cylinders may be achieved by body stencilling or printing or by attached labels to either the body or shoulder, or by the use of neck ring labels etc. The words and phrases may be dispersed if practical constraints prevent them being brought together.

## LPG Cylinder Handling

      1. Cylinders containing LPG are designed to give liquid or vapour off-take.

Vapour off-take must be used in the vertical position.

Liquid off-take must be stored and used in the position indicated on the cylinder.

      1. Where a safety valve is fitted, LPG cylinders are always to be handled in the upright position, valve uppermost, to ensure the correct operation of the safety valve.

      1. Where applicable suitable handling equipment is to be provided in order that cylinders can be handled efficiently and safely without damage to either the cylinder or danger to the individual. Personnel handling cylinders are to ensure that the process has been risk assessed and that they wear the appropriate PPE (refer to Part 2, Chap 2).

      1. Always check cylinder connections and hoses regularly and replace hoses as soon as you spot cracks. Reveal leaks by applying soapy water to all connections - where there are bubbles, there are leaks. Tests for suspected leaks are not to be made with a naked light. Recommended leak detection equipment is detailed in Part 2, Chap 7.

      1. Remember that LPG is heavier than air and will not disperse in a confined space. Do not allow the vapour to enter drains or ducts.

      1. Change or connect LPG to an appliance in the open air. Always use the appropriate PPE (refer to Part 2, Chap 2).

      1. Ensure LPG appliances are used only in well-ventilated areas.

      1. Never smoke or have a naked flame near a LPG cylinder which is being changed. Beware of sparks from electrical tools, grinders, welding equipment, cooking equipment etc.

      1. If you smell the distinctive odour of LPG turn off the gas and get the appliance checked. Avoid inhalation of vapour.

      1. The actions to be taken in the event of a LPG leak are detailed in JSP 319 and Part 2, Chap 5.

      1. No attempt is to be made to heat a receptacle. If the cylinder or the labelling appears to show heat or scorch marks do not use the cylinder. Seek advice immediately from the supplier or the FLC.

WARNING: Users should be aware that an LPG cylinder involved in a fire may fail catastrophically, resulting in Boiling Liquid Expanding Vapour Explosion (BLEVE). DO NOT attempt to extinguish a cylinder that is alight (see JSP 319 and Part 2, Chap 5 and 6).

      1. Filled receptacles are to be capped, and plugs fitted where applicable during storage and transportation. Caps or plugs are not to be removed without making sure that the receptacles valve is closed.

      1. Valves on empty receptacles are to be closed, capped or plugged and if supplied, the valve protecting cover is to be in place.

      1. Empty expendable cartridges are to be treated as potentially dangerous waste particularly if significant numbers are to be disposed of. Units are to contact their FLCs to ascertain the extant disposal instructions.

      1. Store spare cylinders outside but not below ground level. Cylinders are not to be stacked unless designed to do so. The maximum height of unpalletised cylinders is not to exceed 2.5m. The distance between palletised and unpalletised stacks should not be less than 1.5 m and where access is required for mechanical handling equipment (MHE) this distance should be a minimum of 2.5m.

      1. The maximum amount of LPG that can be stored vertically in any one column is to be in accordance with Table 18.2. Further information on the storage of LPG gas cylinders can be found at Annex B to this Chapter.

Table 18.2 – maximum amount of LPG can be stored vertically.
Amount of LPG in any cylinder (kg)	Palletised (kg)	Un-palletised (kg)
<6	35	30
6 - 15	75	45
16 - 20	80	50
21 - 55	110	55

      1. Guidance for the safe handling and storage of LPG cylinders for units whilst on exercise is located at Annex A to this Chapter.

## LPG Cylinder Maintenance

      1. Cylinders are usually owned by the supplier who has the responsibility for their testing and maintenance at the prescribed intervals. MOD personnel are not to carry out any maintenance activities on LPG cylinders. If a suspect or damaged cylinder is encountered the supplier is to be advised after removing the cylinder to a well-ventilated location and applying an Equipment Conditioning Label, (U/S) (e.g. MOD Form 731) detailing the problem. Additionally, if the cylinders are leaking the actions detailed in Part 2 Chap 19 are to be followed.

      1. It is important that all threads of cylinders, valves and seatings are kept free from dirt and foreign matter. No oil or grease is to be used to lubricate the cylinder valves.

LPG Gas Cylinder Storage - General Requirements

      1. This section deals with the various methods of storage of LPG cylinders / cartridges; the requirements of this chapter shall apply unless otherwise stated.

      1. The outside storage of LPG cylinders/ cartridges is the preferred option and should always be considered in the first instance. All permanent fixed storage sites for LPG cylinders/ cartridges are to be the subject of a properly constituted Siting Board (refer to Part 2, Chap 18).

      1. Areas designated for LPG gas cylinder stowage (> 1,000 kg) are not to contain other flammable liquids or gases. Specific guidance on the storage provisions of bulk LPG is given in Part 2, Chap 19.

      1. Separation Distances. Where LPG has to be stored near explosives, advice from the appropriate ammunition technical authority is to be sought.

      1. DSEAR. Outdoor LPG cylinder storage areas can be considered as non-hazardous places in the sense of DSEAR only if:

The outdoor LPG cylinder storage areas is designed, constructed, maintained, and managed fully in accordance with this document and;

The cylinders stored are complaint LPG cylinders, sourced from the current MOD contract.

The operator shall, shall as a minimum conduct a Stage 1 DSEAR risk assessment in accordance with JSP 375. Irrespective of the caveats at the paragraph a and b above; If the Stage 1 risk assessment identifies a dangerous process or explosive atmosphere, then the Stage 2 risk assessment / mitigation process detailed in JSP 375 shall be carried out.

As a flammable gas, a documented risk assessment of the LPG storage area and its surroundings is required under DSEAR; and all workplaces where an explosive atmosphere may occur must be classified into hazardous and non-hazardous areas. Hazardous areas must be classified into zones by a Competent Person (refer to JSP 375).

Vehicular Movement. Strict controls on the access of vehicles and other Mechanical Handling Equipment (MHE) into the LPG cylinder storage facility (only) shall be exercised in accordance with guidance given in Part 2, Chapter 17 . Only vehicles and other mechanical handling equipment associated with transfer and handling operations should be allowed in. Transport vehicles should have their engines and auxiliary equipment, e.g. radios, turned off when cylinders/ cartridges are being loaded or unloaded.

Where non explosion protected Mechanical Handling Equipment (MHE) is used in LPG cylinder storage facilities only, a specific risk assessment must be carried out. Examples of processes to be considered as part of the RA, (list not exhaustive) are:

Amount of LPG cylinders stored.

Storage facilities (indoors / outdoors).

Ventilation.

Design of MHE (use of non-spark ignition powered MHE, diesel / battery powered, NOT petrol /LPG).

Ignition hazards.

Flashback form air inlet system.

Spark arrest (exhaust).

Use of engine air shut off valves (“Chalwyn valves”).

Use of non-ferrous / non sparking forks.

Training.

Gas measurement.

Emergency procedures.

Non explosion protected MHE shall be removed from LPG storage areas when the activity is completed.

Where non-explosion protected mechanical handling equipment is used, special precautions shall be taken in respect of design of pallets and operator training.

Signage. The LPG warning sign as depicted in Chapter 17 (Figure 17.1) to this document shall be displayed on each side of the fenced storage area that represents an approach route. All other relevant signs and pictograms detailed in Figure 17.1 shall be displayed.

Fire Safety. Each storage location shall be provided with a minimum of two fire extinguishers suitable for use on a Class C (gases or liquefiable gases) fire. The quantity and type of fire extinguishers required is to be risk assessed by DFRMO fire safety personnel.

## Outdoor LPG Cylinder Compounds, LPG Cylinders (≤ 20kg Individual Size; Total Storage Capacity ≤ 400kg)

Siting. The LPG Industry COP 7 allows for less stringent procedures where the individual cylinder size does not exceed 20 kg and the total storage of LPG does not exceed 400 kg. Examples of this type of storage are included in Annex B; but it is re-iterated that authority from DFRMO must be sought in the first instance when this type of storage is being considered. Additionally, a risk assessment (refer to Part 2, Chap 1) must be made of the proposed site to ensure that the LPG storage does not pose an unacceptable risk to human life and property.

Pictorial examples of the various LPG cylinder options are shown at Annex B.

Construction and Layout. Where LPG cylinders are stored against a boundary wall it must be with the owner’s consent. The wall is to be at least 2 m high and provide at least 60 minutes fire resistance.

The wall must be imperforate for a distance of 1 m either side of the storage area. The LPG cylinders are to be at least 2 m from any building opening and at least 3m from other flammable materials. The height of the stack is not to exceed the height of the wall.

If LPG cylinders are stored against a building wall, the area up to 2 m either side of the storage area and up to 9 m above ground should have no openings and be of 60 minutes fire resisting construction. Any overhanging roof should also be constructed of 60 minutes fire resisting construction.

A building that houses vulnerable populations is not to be considered for the storage of LPG cylinders.

There should be no overhanging eaves or similar projections made of combustible materials above any cylinder. No external stairway or fire escape is to be positioned above stored LPG cylinders and no access or escape route should be compromised by the storage area.

Passageways shall not be used as storage areas.

LPG cylinders may be stored in a corner between two walls (refer to Annex B, Figure 18.B.2 to this Chapter).

If the storage area has 3 walls at least one should not exceed 3m in height.

LPG cylinders may be stored between two wing walls (refer to Figure 18.B.4 to this Chapter). If the wings are less than 2 m high, they should be discounted for separation purposes and the area considered as if it were located against a single wall. If the wing walls are 2 m or higher, separation distances may be calculated by measuring along and around the perimeter. To ensure adequate ventilation the wing wall should not extend outwards more than 1 m beyond the storage area.

## Outdoor LPG Cylinder Compounds, LPG Cylinders Storage Capacity (> 50kg ≤ 1000 kg)

Siting. The chosen site shall be well ventilated to allow for dispersal of gas from small leaks, level and the base must be sufficient to support the weight of the gas cylinders. Examples of typical outside storage layout are at Annex B.

Whenever possible, LPG cylinders shall not be stored in open areas on hard standings.

Unless the storage area is contained within a larger protected area or where 400 kg or less of LPG is stored, the storage compound shall comply with the requirements given in this Chapter. However, the requirements of Para 43 of this Chapter, Access and Egress, may be relaxed in respect of the provision of a single door, provided that the maximum escape distance from any part of the storage area to the exit measured around the LPG cylinders does not exceed 9 m.

Construction and Layout. In temperate climates it is not usually necessary to provide overhead cover to reduce the effects of direct radiation. In tropical climates the requirement for overhead cover shall be the subject of a risk assessment. Where overhead protection is deemed necessary it shall be high enough above the cylinders not to impede the natural ventilation and should reflect the sun’s rays. The store shall be constructed from non-combustible material.

The separation distances that apply to the outside storage of LPG cylinders are given at Annex A to this Chapter. This also includes the reduced distances permissible when a fire-wall is incorporated. Irrespective of the separation distances given in Annex A, the minimum distance from the storage perimeter fence to the nearest LPG cylinder shall be 1m for nominally empty cylinders and 1.5 m for full cylinders.

Where vulnerable populations are housed, the minimum separation distance for LPG stored in excess of 400 kg shall be 8 m or that given in, Annex A whichever is the greater distance. Where a fire-wall or other fire resisting separation is incorporated this minimum distance may be reduced in consultation and on the authority of the regional DFRMO officer.

There shall be no opening into buildings, cellars or pits within 2m of an LPG storage area or the separation distance given in Annex A whichever is the greater. In exceptional circumstances where a gully or drain is unavoidable within 2m the opening shall be securely covered or fitted with a suitable seal to prevent the entry of vapour.

## Outdoor LPG Cylinder Compounds - Storage of LPG Cylinders Within a MTFI

Siting. Within Motor Transport Fuelling Installations (MTFI) it is acceptable to store small quantities of LPG cylinders where an alternative gas cylinder storage compound is not available. The hazards associated with locating cylinders at a fuel site shall be assessed and as necessary any risks mitigated. Reference shall be made to JSP 317.

Note: The storage of LPG in a cage shall be included within the fuel site safety case and is auditable as part of the Fuel and Gas Safety Assurance programme.

The cage shall be located in a well-ventilated position.

The cage shall be protected from, or not to be located where it can be struck by, vehicle movements.

The cage shall not be located where it can become immersed in fuel following a spill.

The location of the cage shall comply with the minimum safety separation distances within Annex A to this Chapter. A minimum separation distance of 4.3m from fuel pumps and fuel storage tank man-lid shall be required.

There shall be no openings into buildings, cellars, pits or confined spaces within 2m.

There shall be no parking of vehicles with 3 m of the cage

Construction and Layout. Cylinders shall be stored in a dedicated wire cylinder cage. The mesh on the cage shall be small enough to prevent any unauthorised tampering, especially with the valves. The cage shall be kept secured.

The maximum quantity of LPG to be stored shall be 400kg.

Nominally empty or part used cylinders shall be treated as full for the purpose of storage in this cage.

The cage shall be maintained in a serviceable condition and shall be regularly inspected for continued fitness for use.

Signage. All relevant safety signs and warning notices detailed in Chapter 17 - Figure 17.1 to this Chapter document shall be displayed, including the emergency actions and contact details.

## LPG Cylinder Storage, Inside Specially Constructed Buildings

The permissible quantity of LPG to be stored is detailed at Annex A, Table 18.A.2.

Access to the building is to be restricted to authorised persons only.

Siting. The preferred method of storage of LPG cylinders is in the open. Where for security or climatic reasons LPG cylinders shall be stored in buildings the preferred option is within a purpose built structure.

Examples of typical purpose-built LPG cylinder stores are shown at Figure 18.B.7 and Figure 18.B.8.

Separation Distances. The separation distance from the store to the boundary, other buildings or fixed sources of ignition is determined by the capacity of LPG stored and shall be in accordance with that detailed at Annex A to this Chapter.

Where the minimum separation distance to the boundary as detailed at Annex A (other than a building or fixed source of ignition) cannot be met, the appropriate external and internal walls are to provide a minimum of 60 minutes fire resistance; and internal walls are to have no ventilation openings.

Construction and Layout. No part of the building is to be below ground level.

The building shall be mainly constructed from non-combustible materials. Roof supports (including load bearing capacity) shall provide a minimum of 60 minutes fire resistance.

At least half of the longest wall or half of the roof area shall be constructed from open mesh or lightweight materials to act as explosion relief. The relief should ensure that any explosion is safely vented and that parts of the building do not present a subsequent hazard.

The floor of the storage room shall be level and able to support the weight of the cylinders. There shall be no drains, ducts or sumps.

The number of doors is dependent on the layout of the building. The requirements of Para 43 to this Chapter may be relaxed in respect of the provision of a single door, providing the maximum escape distance from any part of the storage area to the exit measured around the receptacles does not exceed 9 m.

Ventilation. The building shall be provided with dispersed ventilation openings totalling a minimum of 2.5% of the combined area of the walls and roof. Ventilation openings shall not be placed in those parts of the building within the separation distances at Annex A to this Chapter.

Zoning. A documented risk assessment of the indoor LPG cylinder / cartridges storage facility and its surrounding areas including areas adjacent to the building’s ventilation openings, shall be carried out in accordance with JSP 375 Part 2 Vol 1 Chapter 9.

Lighting. If required, internal and building located external lighting shall be to Zoned as identified from the DSEAR risk assessment. and give an average luminance of 350 lux in the horizontal plane 0.8 m Above Finished Floor Level. Emergency lighting shall be to the requirements of BS 5266-1 to give a luminance of approximately 2 lux with 3 hours duration.

Signage. All relevant safety signs and warning notices detailed in Chapter 17 - Figure 17.1 shall be displayed. Specifically, the LPG warning sign (i.e. an LPG warning sign together with a No Smoking sign and a Highly Flammable sign) shall be displayed on each side of the building that represents an approach route.

Full and nominally empty LPG cylinders may be stored together in the same building although they are to be segregated and marked by the use of suitable signs such as those depicted in Chap 9 Annex A to this document. Nominally empty gas cylinders shall be treated as full cylinders with respect to hazardous zoning and in calculating separation distances.

Fire Safety. Each storage location shall be provided with a minimum of 2 x Extinguishers. The quantity and type of fire extinguishers required is to be risk assessed by DFRMO fire safety personnel.

## LPG Cylinder Storage, Inside Existing Buildings

Where it is not practicable to store LPG cylinders / cartridges in the open air or in a purpose-built building, exceptionally they may be stored in specially designed storage areas in buildings subject to the following conditions.

The quantity of LPG cylinders / cartridges stored shall not exceed that stated in Annex A Table 18.A.2.

Siting. The use of this area of the building for the storage of gas cylinders shall be included in the building safety plans.

Appropriate controls shall be enforced to minimise any hazard to adjoining rooms, with an assessment of the use of electrical equipment, naked lights and a ‘No Smoking’ policy.

Construction and Layout. The building shall be one storey and shall not be used for sleeping accommodation.

At least one side of the store shall be an external wall of the building.

The doorway into the store shall be located in an outside wall. Alternatively, a ramp or sill of at least 250 mm shall bridge the doorway in order to prevent LPG vapours entering other parts of the building.

There shall be no drains or other openings in the floor.

Explosion relief shall be provided equivalent to half the area of the longest wall. The explosion relief shall be located in an outside wall or roof and vent to a safe place. The relief area may be left open or covered with wire mesh or lightweight panels.

Any part of the front of the building, including any overhanging roof, up to a height of 9 m and extending horizontally for a distance of 2 m on either side of any opening into the storage area shall be imperforate and of 60 minutes fire resistance. Any openings in the fire resisting section shall be fixed shut and appropriately protected.

Ventilation. Well dispersed natural high and low level ventilation shall be provided in the form of permanent openings in the outside wall equal to a minimum of 12 % of the area of one of the outside walls or 2.5% of the total area of the walls and roof whichever is the greater.

Ventilation shall not discharge directly onto accommodation or office areas, areas where people accommodate, onto a pavement, or compromise any escape route; and the separation distances for apertures and other points shall be in accordance with Annex A to this Chapter. Ventilation discharge areas shall be designed as “No Smoking” areas.

Signage. The external walls of the building and adjoining internal walls shall be suitably labelled (refer to this Chapter 17) to assist firefighting and security operations in identifying the hazards and risks inside the building.

## Gas & LPG Cylinder Storage on Operations and Exercises

General. Where it is necessary to provide temporary facilities for the storage of gas cylinders on military operations and exercises the requirements of JSP 319 are to be followed. However, where it may be impracticable to fully comply with the requirements detailed in JSP 319, the following procedures are to be followed.

Protection against Terrorism. Gas cylinder storage areas are potential terrorist targets. This is a particular concern for gas cylinder storage areas located in Out of Area Operations. Unit management are to take the potential terrorist threat into account when siting gas cylinder stores; the gas cylinder store manager is to ensure the security of the gas cylinders held within; and the safety of the personnel required to work in the local area.

A written assessment of the site is to be carried out by the senior person responsible for the storage site. The assessment is to identify and to include mitigation against all potential hazards (refer to Part 2, Chap 1). The risk assessment is to be approved by the senior officer responsible for the operation / exercise.

Where available, an existing dedicated facility is to be used.

Operations / Exercises. Where practicable, storage of all gases on operations / exercises shall be as for non-operational storage. Those elements that cannot be achieved without compromising operational effectiveness may instead be risk assessed and the risks mitigated as far as possible by the Delivery Duty Holder (DDH), with the risks entered on the corporate risk register. Only when assessing the risk in an operational theatre, may the risk to operational effectiveness be given higher priority to the risk of life; when this is done, the operational commander (DDH/ ODH) shall give explicit authorisation.

Where practicable, gases shall be supplied using the current MOD gas supplier. Where this is operationally unfeasible, the DDH shall ensure that gases and cylinders supplied from local sources are to the same quality standard and specification as that provided by the MOD contract. Locally sourced gases and cylinders shall be risk assessed and the risks mitigated as far as possible by the DDH, with the risks entered on the corporate risk register.

Where local gases and cylinders are procured (including LPG cylinders), any deviations from the standard gas cylinder markings as detailed in Part 2, Chap 3 shall be notified within the operation / exercise order. As part of the operational / exercise administration instruction; guidelines are to be included concerning the safe storage and handling of all cylinders.

Refer to Part 2, Chap 18, Annex C for guidance on siting LPG cylinders in the field.

An aide memoir to assist in the siting of LPG cylinders in the field is at Part 2, Chap 18, Annex C.

## Additional Requirements for Gas Cylinder Storage on HM Ships and Other Vessels

1. Gas cylinder storage specifications and safe storage procedures shall be approved for HM ships by Director General Ships and for other Service vessels by the appropriate authority. Reference is to be made to DBR 1754.
# Annex A - Minimum Recommended Safety Separation Distances for LPG Gas Cylinders

Table 18.A.1- Minimum Separation Distances for LPG Storage in Cylinders and Cartridges
Total Qty of LPG Storage (kg)	Size of Largest Stack (kg)	Minimum distance from nearest cylinder to boundary, building or fixed ignition source where:
		No fire wall is provided (m)	A fire wall is provided (m)
15 – 400	< 1,000	1	Nil
401 – 1000	≤ 1,000	3	1
1,001 – 4,000	≤ 1,000	4	1
4,001 – 6,000	≤ 3,000	5	1.5
6,001 – 12,000	≤ 3,000	6	2
12,001 – 20,000	≤ 5,000	7	2.5
20,001 – 30,000	≤ 7,000	8	3
30,001 – 50,000	≤ 9,000	9	3.5
50,001 – 60,000	≤ 10,000	10	4
60,001 – 100,000	≤ 10,000	11	4.5
100,000 – 150,000	≤ 20,000	12	5
150,001 – 250,000	≤ 30,000	15	6
> 250,000	≤ 30,000	20	7

            1. LPG Industry Codes of Practice 24, Part 1 and BS 5482 specify a distance from LPG cylinders and “readily ignitable materials” which should not be less than 1 m. “Readily ignitable” in terms of oil tankers means those containing products having a flash point of 65°C or less.

            1. This includes most domestic heating oils. The separation distance of 1 m is to be maintained even if the flash point is above 65°C.

Table 18. A.2 - Quantity of LPG storage Within a Building
Type	Max quantity of LPG per compartment (kg)	Max number of compartments	Max total quantity of LPG in building (kg)
Specially designed single storey building
Cylinders & Cartridges	5,000	5	25,000
Cartridges only	50,000	5	250,000
Specially designed storage space within an existing building
Cylinders & Cartridges	1,000	1	1,000
Cartridges only	5,000	1	1,000

            1. Where storage buildings do not fall within a larger adequately secured area, the separation distances in Table 9.B.1 should be enclosed by an industrial type security fence at least 1.8 m in height. Fire walls or other buildings may form part of this separation distance.

Table 18. A.3 - Additional Minimum Safety Distances for LPG Cylinders at a MTFI
Event	Safety Distances
Fuel tank vents and fill points	7.5m
Fuel dispensers	7.5m
Flammable liquid bunds	3m
Parked vehicles	6m
Vehicle being fuelled	3m

# Annex B - Design and Layout for LPG Gas Cylinder Storage Areas - Examples

Figure 18.B.1- Storage of 400 kg or Less Against a Building

Figure 18.B.2 - Storage of 400 kg or Less of LPG in a Corner

Figure 18.B.3 - Storage of 400 kg or Less of LPG against a Boundary Wall

Figure 18.B.4 - Storage of 400 kg or Less of LPG between 2 Wing Walls

Figure 18.B.5 - Typical Outdoor LPG Cylinder Store (Within a Site to which Access to LPG is not Otherwise Controlled

Figure 18.B.6 - Typical Compound for Storage of LPG Cylinders

Note: For minimum distances from any gas cylinder to buildings, boundaries and sources of ignition see Annex A. Part 2 Chapter 18

Figure 18.B.7 - Indoor LPG Cylinder Storage within a Specially Designed Storage Room within a Building.

Figure 18.B.8 - Indoor LPG Cylinder Storage within a Specially Constructed Building.

# Annex C - Unit Guide to the Safe Handling and Storage of LPG Cylinders on Exercise

General

1.	Handle cylinders with care and avoid damaging the valve.

2.	Always store cylinders upright.

3.	Always ensure that valve protectors are fitted and secure.

4.	Only store the minimum number of cylinders necessary.

5.	Do not store LPG cylinders with fuel, lubricants, oils, greases, ammunition or any other hazardous or readily combustible stores.

6.	Do not allow smoking or naked lights near LPG.

7.	Do not place cylinders in locations that will hinder escape in an emergency.

8.	Do read the safety data sheets and learn the hazards associated with LPG.

Site Location

9.	Level and firm enough to support the cylinders. Limited quantities of LPG may be left on wheels. Ensure the canopy is rolled up to provide maximum ventilation.

10.	If storage is indoors, the building is to be well ventilated and not used as sleeping accommodation.

11.	Only store cylinders on the ground floor and do not block escape routes. Never store cylinders in cellars or below ground level.

12.	Avoid areas close to drains pits and gullies and do not store beneath power lines.

Fire Precautions

13.	Provide a minimum of two fire extinguishers suitable for use on a Class C (gases or liquefiable gases) fire. It is recommended that these should be 2 x 9 kg dry powder extinguishers.

14.	Keep the area surrounding the cylinders free from combustible materials as far as is practicable.

15.	Ensure that emergency drills are known and practised.

Action on Discovering a Leaking Cylinder

16.	If the cylinder is not ‘a light’ and it is safe to do so, the cylinder valve should be closed (remember that escaping gas can cause the exit point to become very cold causing frost burns if touched).

17.	Evacuate people from the immediate area and isolate and identify the damaged cylinder.

18.	If the cylinder is alight raise the fire alarm. Do not attempt to extinguish the flame from a leaking cylinder.

# 19 - Bulk LPG

Chapter Sponsor - DIO TS Eng Gas AH

## Scope

  1. This chapter details specific requirements for selecting a site for bulk LPG storage, including the requirements of a siting board, and acceptance or handover board, and the requirement to notify and/or obtain planning consent from local authorities for Bulk LPG storage sites. It also includes the requirement for compliance with DSA 03 OME Part 4 Defence Major Accident Control Regulations (MACR).

## Notification to Civilian Authorities of LPG Facilities

  1. If more than 25 Tonnes of LPG is stored on site, the Commanding Officer, or Head of Establishment is responsible for complying with the Notification of Installations Handling Hazardous Substances Regulations, 1982, requires that the Health and Safety Executive be informed. Local Authority consent is also required under the Planning (Hazardous Substances) Act, 1990, and the Planning (Hazardous Substances) Regulations, 1992. Similar regulations apply in Scotland.

  1. The Dangerous Substances (Notification and Marking of Sites) Regulations, 1990, requires the local Fire Authority and Health and Safety Executive to be informed when 25 tonnes or more of dangerous substances, including LPG are to be stored. Hazard warning signs to be installed at all access points.

  1. Notification is to include, in each case, the following:

Name, address and official capacity of the person making the notification.

Full postal address and grid reference of the LPG installation.

The area of the installation covered by the notification and details of adjacent sites.

The date storage is to commence.

A general description of the activities to be carried out at the installation.

The name and address of the planning authority covering the installation.

The type of product to be stored [e.g. propane, butane], the maximum quantity to be stored, and the maximum storage capacity including pipelines.

Where the quantity of a controlled substance reaches the lower tier threshold (in this case 50 tonnes of LPG), those responsible for the project must ensure that the requirements of the Control of Major Accident Hazard Regulations, (COMAH), 1999; the The Control of Major Accident Hazards Regulations 2015.; and the Planning (Control of Major-Accident Hazards) Regulations 1999 are met. Separate, but equivalent or comparable regulations exist for Scotland and Northern Ireland. This requires the preparation of a Major Accident Prevention Policy (MAPP). In addition, sites holding quantities above the top tier threshold (in this case 200 tonnes of LPG) must also submit a Safety Report in which they demonstrate that all measures necessary have been taken to prevent major accidents and limit their consequences.

The COMAH Regulations, which are the UK implementation of a European Union Directive, do not apply to Military Forces and Defence Establishments of European Union Member States. The equivalent MOD Regulations are the Major Accident Control Regulations – DSA 03 OME Part 4 Defence Major Accident Control Regulations (MACR) and these regulations are enforced by the MACR Controlling Authority (MACR CA). MAPPs and Safety Reports for Military Forces and Defence Establishments must therefore be submitted in accordance with the requirements of DSA 03 OME Part 4 Defence Major Accident Control Regulations (MACR).

## Bulk LPG Road Delivery Precautions

As part of the bulk LPG siting process adequate provision should be made for the safe access and egress of bulk LPG delivery vehicles within a fenced compound, wherever practicable. Ad hoc arrangements whereby LPG supply hoses are run across a public footpath or pavement from a delivery vehicle, or run over fencing should be avoided where possible, if no alternative is available the delivery process is to be risk assessed and mitigations implemented to reduce the risks to ALARP.

Road Tanker delivery area shall be separated from other traffic movement areas. This can be achieved by a specific lay by or road barriers to prevent pedestrian / vehicular movement in an area whilst LPG delivery taking place. LPG deliveries from delivery vehicles to bulk vessels have the potential to release LPG, therefore this activity is governed under DSEAR. Therefore, a DSEAR risk assessment shall be carried out. (Refer to JSP 375, Vol 2 Chapter 9)

Road Tanker drive-away protection/prevention devices (signage) shall be in place to ensure a hazard cannot occur if the vehicle is moved before a delivery hose is disconnected. Demonstrated either by: -

Contractor - purpose designed vehicle.

Or- signage at delivery point.

Safe vehicle access may include:

Level ground, or a slight camber to direct spillage away from the tanker.

A clear line of sight for the controller to see both the delivery tanker and the LPG storage vessel(s) being replenished.

The provision of bollards or crash barriers to protect storage vessels and pipelines, as fences, signs and warnings alone do not provide physical protection.

Fire extinguishers.

Warning signs to be erected during product transfer stating “WARNING
FLAMMABLE GAS TRANSFER, NO SMOKING OR NAKED LIGHTS” or similar
words, in accordance with BS 5499 - Safety Signs and Colours Standard and the Health and Safety (Safety Signs and Signals) Regulations 1996.

LPG transfers to be carried out under the direct control of a Responsible Person and discontinued if that person is called away.

If deliveries take place during the hours of darkness then adequate lighting, to Zone 1 or 2, as appropriate, must be provided (see Annex A).

The bulk delivery vehicle should be bonded to earth, or bonded to the storage vessel bonding point, as appropriate, before delivery commences.

Bulk LPG vessels should not be bunded; however, they may be protected by diversions kerbs, not exceeding 500 mm in height, designed to divert LPG spillages away from storage vessels and potential sources of ignition to an Evaporation Area. The Evaporation Areas should be located in a safe area at least 3 m away from the storage vessel. It should be surfaced with stone chippings, or similar material, to increase the surface area and promote evaporation and dispersal of the LPG gas. See LPG Industry Codes of Practice 1 for further details.

Areas outside the fenced LPG Hazardous Area should also be kept free from a build-up of combustible materials such as fallen leaves and grass cuttings, old pallets, etc. Any fires that may break out in these areas are a potential threat to the safety of the LPG installation and, where possible to do so, should be tackled at an early stage before the threat to the LPG storage area escalates (see Part 2, Chap 19, Annex A).

Appropriate steps must be taken to prevent unauthorised interference with storage and or equipment and plant. If fencing is erected, then at least two means of escape should be provided. All emergency exits are to open in the direction of escape and are to be fitted with panic furniture of a type not requiring a key, card or code to open. They are to provide an unobstructed means of escape and in operation are not to obstruct any other escape route. Any installed fire walls can be regarded as part of the security fencing.

Bulk LPG Siting Boards and Siting Requirements

This Section summarises the considerations that apply to the siting of bulk LPG storage vessels. It is based on LPG Industry Codes of Practice 1, Parts 1 and 2 and as such does not cover all the considerations that are needed for buried and mounded LPG storage vessels. See LPG Industry Codes of Practice 1, Part 4.

The proposed storage site should be surveyed for any possible hazards, including overhead cables, fixed sources of ignition and ground conditions. Bulk LPG should not be stored in buildings; it should be stored outside in well ventilated areas away from fixed sources of ignition and avoiding open pits, hollows and ground depressions where leakages may collect. Tables 19.A.1 and 19.A.2 in provide minimum separation distances between LPG storage vessels; between LPG storage tanks fixed ignition sources, buildings and site boundaries; and between LPG storage vessels and other hazards / hazardous materials, such as flammable liquids and liquid oxygen.

Bulk LPG storage vessels should be properly installed on firm foundations & supported on concrete, masonry or structural steel supports. These supports should be so constructed or protected to ensure their load bearing capacity is maintained for same period as fire resistance for vessel.

The ground beneath the LPG vessel shall be concrete or compacted & arranged to prevent pooling of spilled product. (Does not have to be the whole of the surface areas of the installation- recommend stone chippings).

Bulk LPG storage vessels >2.2. Tonnes capacity (or where piers are used as part of vessel support). The Vessel shall be supported at one end only. The secured end is where principal liquid & vapour lines are attached.

Bulk LPG Storage Vessels shall be provided with visible, legible, & indelible markings:

Pressure (Px) vessel design code

Manufacturer name

Vessel Serial No

Max / Min design Px (bar)

Max / Min operating Temp

Vessel Date of Manufacture

LPG Storage Vessel should be provided with visible, legible, & indelible markings:

Water capacity in Litres

Date of test, px applied, inspection authority’s identification

Provision for subsequent test marking

Bulk LPG installation – compound security. The installation shall be surrounded by a suitable secure open mesh or palisade fence that is:

1.8m high

Has 2 means of exit (on opposite sides with outward opening gates) (see Para 16) of this chapter.

Distance from the bulk LPG storage vessel to the fence shall be 1.5m.

LPG compounds for supply to Autogas refuelling sites (LPG dispensers), or to multiple consumers, (e.g. Service Family Accommodation metered estates), where the public or Service Families have uncontrolled access (without a site / camp perimeter), shall be enclosed by a fence, but shall be 3m from the vessel.

If the storage vessel is located where there is constant 24/7 attendance (vessel is visible to site staff directly or via closed circuit TV); then the distance between the vessel and fence may be reduced to 1.5m. Provision for a security fence can be relaxed if:

The LPG vessel is less than 4 Tonnes capacity.

Access to valves & fittings on the tank are denied (lockable hinged cover).

There is no uncontrolled public access within the proximity to the LPG vessel (DTE- National Parks)

Ideally, bulk LPG should not be stored in the same compound as gas cylinders, flammable liquids or liquid oxygen; but in all cases the minimum safety separation distances, given in Tables 19.A.1 and 19.A.2 shall be observed for LPG vessels located above ground.

## Bulk LPG Installation Design

The design of the bulk LPG storage vessel is the responsibility of the Contractor leading the construction project. However, the MMO shall ensure that any such vessel complies with current design and build standards. The location and layout of bulk LPG installation is the responsibility of MOD (DIO / MMO) and should be carefully considered to ensure:

Adequate separation from other hazards, such as fixed sources of ignition, ammunition stores, bulk fuels and lubricants, flammable stores, bulk liquid oxygen, etc.

Adequate separation from site boundaries, buildings, public roads, runways, etc.

Site accessibility for the ground works, delivery and installation of the storage vessel(s).

Adequate free ventilation.

Accessibility for LPG delivery tankers (access and egress, particularly in the event of an incident occurring).

Accessibility for firefighting.

Water supply for fire brigade use.

Clear line of sight for LPG delivery drivers between the delivery tanker and the storage vessel(s).

Storage vessels not to be sited under electricity or phone cables, trees or overhanging tree branches, car ports or roof eaves.

Storage vessels not to be sited where damage from cranes, gantries or other overhead structures may occur.

Buried LPG storage vessel(s) not to be sited in areas subject to flooding, or close to Party Walls.

No open drains, gullies or ducts located within the vessel safety distances (see Tables 19.A.1 and 19.A.2) unless they protected from access and passage of LPG vapours.

No underground services to pass under the foundations of the LPG storage vessel(s).

In the case of multiple LPG storage vessel, adequate siting so that spillage from one vessel does not affect other vessels or adjacent facilities.

Safe passage for LPG gas pipe line(s) to service locations.

Suitable location(s) for Evaporation Area(s) to allow spillages from LPG delivery vehicle and LPG storage vessel(s) to be diverted to a dedicated area where it may safely evaporate (see Para’s 14 & 20 of this chapter). The use of an indicator, such as a windsock or other device, to provide in the early stages of any spillage or leak an indication of which neighbourhood might be exposed to plumes and/or ground strike is recommended.

The Acceptance/Handover board should check that the considerations discussed above have been adequately resolved. In addition, the following should be assessed:

Physical security, such as fence around bulk LPG storage area or other access controls.

Physical protection of storage vessels and pipelines from vehicles, e.g. bollards or curb stones.

Means of escape, such as outward opening exits. (Para 16) of this chapter.

Adequate means of firefighting. The provision of portable fire extinguishers at LPG compounds shall be based on the results of the Fire Risk Assessment, carried out by the competent person iaw current fire safety regulations (Regulatory Reform (Fire Safety) Order 2005). However, the LPG Industry Code of Practice 1, Part 1, Table 8 sets out good practice and minimum fire precaution recommendations for above ground LPG installations.

Adequate signage, including safety signs and warning notices, are displayed around the boundaries of the storage area; pipe lines are labelled; and all LPG system and building stop valves both labelled and with provided with operating instructions.

Emergency telephone numbers, including the LPG supplier’s 24-hour emergency telephone number, are prominently displayed.

Training and Standard Operating Procedures.

Absence of fixed sources of ignition or the presence of other hazards within the minimum separation distances between bulk LPG and site boundaries, buildings, fire walls, etc.

## Demarcation of Site Responsibilities

Bulk LPG storage vessels are owned by a Contractor and are leased to the MOD. However, the bulk LPG installation is a MOD owned asset, whereby the leased vessel is but part of the LPG storage and supply system. Even though DIO (MMO) has no direct maintenance responsibilities for the bulk LPG storage vessel; DIO (MMO) still maintains the responsibility to ensure that the system (the bulk LPG installation) is a safe place. As such, DIO, MMO shall demonstrate that maintenance procedures and operating procedures are in place for all activities that occur in or within the vicinity of the bulk LPG installation.

Once commissioned, the Operating Authority will have to gain access to the bulk LPG installation, (e.g. to carry out gauge content reading, prior to ordering LPG deliveries). As part of the take-over process, the MMO / Contractor shall arrange for any necessary installation specific familiarisation training required by the RP Gas, the maintainer, and the operators of the installation as applicable. An appropriate record of those personnel who have received training shall be maintained by the recipient and RP Gas in accordance with JSP 375 Vol 3 Chapter 8.

## Automotive Mechanical Transport Fuelling Installation - General

This chapter details the specific requirements for Automotive LPG Mechanical Transport Fuelling Installations. On MOD estates, Automotive LPG Mechanical Transport Fuelling Installations (LPG Dispensers) are used to issue LPG into Auto gas powered vehicles. These facilities are found on the MOD estate as standalone assets, leased from the gas supplier and are mainly used by flying/gliding clubs to fuel LPG powered motorised winches.

The source document for any unit intending to construct a LPG MTFI is LPG Industry Code of Practice 20. Project managers are to ensure that the COP 20 is the extant version issued by the Liquid Gas UK. Reference must also be made to Defence Estates publications SRP CER, SRP 02 and SRP 03. As systems for delivering LPG in liquid form, they will fall within the scope of SRP 03; and come under the control of AP (Petroleum).

Anyone involved in the design, installations are to be aware of the properties and potential hazards of LPG, as detailed in Part 2, Chap 1, Para 14 ‘Hazards’ & Table A.3 for LPG Properties.

Under the Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) all hazardous areas, i.e. an area where an explosive atmosphere may occur, are to be zoned. LPG leakages from a MTFI should be low and the likelihood of an ignition extremely low provided that adequate precautions are taken, and the necessary warning signs are display.

Portable Extinguishers. Firefighting equipment must be selected and installed in accordance with the Defence Infrastructure Fire Standards and be based on the findings of the Fire Risk Assessment IAW the Regulatory Reform (Fire Safety) Oder 2005 (as amended . However, Liquid Gas UK recommend that at least 2 x 9 litre dry powder extinguishers to BS EN 3 or equivalent, suitable for LPG fires with a test fire rating of at least 21A and 183B as defined in BS EN 3-7, are to be located at the installation control point. In the event that the dispensers are separated from the control point by more than 15 m an additional extinguisher is to be located at the dispenser.

Security. Adequate steps are to be taken to prevent the unauthorised interference with vessels, dispenser and ancillary equipment. If fencing is to be used, at least two means of exit are to be provided. The exit gates are not to be adjacent to each other and all gates must open outward.

A system to protect vessels and dispensers from vehicular damage is to be installed. The installation, when closed is to be protected against interference and unauthorised operation by:

Isolation of all electrical supplies is to be by means of a mains switch, to be readily visible and within easy reach for quick operation in an emergency.

All ancillary equipment is to be contained within a lockable well-ventilated cabinet.

Where pumps switches are external to the dispenser cabinet, the cabinet doors are to be secured when not in use.

A means of securing the refuelling nozzle to the dispenser holster is to be supplied.

Safety signs and warning notices. Appropriate signs and notices are to be displayed in-line with Part 2, Chap 17, Figure 17.1. In addition, the following signs shall be displayed:

HIGHLY FLAMMABLE – PROPANE NO SMOKING

Figure: 19.1 - Additional safety signs and notices for LPG storage

The following sign is to be displayed at the installation dispensing pump emergency isolator switch.

Figure: 19.2 - Signage at the master switch

## Operations

Written Procedures. Standard Operating Procedures (SOPs) are to be established so all personnel understand their duties during normal operations, the closing of the refuelling installation and the duties required upon a receipt of LPG from a delivery tanker. SOPs are to be put in place to ensure all personnel are aware of the actions to be taken in the event of an emergency incident occurring. For reporting of incidents/accidents see JSP 319 defet homepage.

Self Service - Vehicle Refuelling by Vehicle Driver. Self-service refuelling of LPG vehicles shall only be permitted if a fully trained competent person, conversant with the procedures for emergency shutdown is in attendance.

The installation manager shall display adequate notices giving instruction on how to operate the dispenser, this notice is to be displayed on or as near as possible to the refuelling island. The instruction shall include the following warning:

If an adapter is required, it must be connected to the vehicle fuel coupling first – not the filling nozzle. If you do not have a correct adapter, request assistance from the attendant: / DO NOT USE FORCE TO MAKE A CONNECTION

Daily Closedown. Installations that operate restricted opening times must be shut down with all electrical supplies to dispensers and pumps isolated at the master switch. Security arrangements are to be put in place to prevent any unauthorised operation or interference.

## Training

Scope of Training. Training is vital to prevent incidents and to minimise the consequences should an incident occur. All personnel employed within the LPG automotive dispenser installation must have adequate training in the proper use, and the action drills in the event of a malfunction of equipment and the ability to deal with any emergency (see JSP 319) operators shall be authorised, and copies of their respective training records shall be held by the respective be held by the respective RP Gas IAW DIO GSMP (Sections A, B & C).

The training may take many forms, including the giving of instructions (verbal and written) and a formal training course. The training should ensure that those who are trained understand:

The hazards of LPG including knowledge of the contents are on the Safety Data Sheet.

The risks within the installation.

The measures to be put in place to deal with the risks.

The correct use of the filling coupling, and the provision of adapter use.

The emergency procedures relevant to the installation (Part 1, Chap 5).

The action required if a drive away with the filler hose connected occurs and the procedure for reinstating breakaway couplings.

The use of all fire equipment applicable to the installation.

Their duties in accordance with local Standard Operating Procedures.

# Annex A - Minimum Separation Distances for Bulk LPG Vessels

            1. Table 19.A.1 provides minimum separation distances for bulk LPG storage vessels, based on vessel capacity, between vessels; and between vessels and buildings, boundaries and fixed sources of ignition, depending on whether a fire wall is, or is not installed.

            1. Table 19.A.2 provides minimum separation distances for bulk LPG storage vessels and other hazards, such as flammable materials, liquid oxygen and electrical cables.

            1. The separation distance between bulk LPG tanks and oil tanks/tank bunds is given in LPG Industry Code of Practice 1, Part 1, Table 2. For oil tanks containing up to 3000 litres of product having a flash point of 65°C or less and LGP tanks up to 60 tonnes this distance is 3m. To allow access and ventilation to the LPG tank the separation distance between bulk LPG tanks and oil tanks containing products having a flash point of more than 65°C should not be less than 1m.

Table 19.A.1 - Minimum Separation Distances for bulk LPG vessels
Maximum LPG Capacity			Minimum Separation Distance (m)
Any single vessel in a group		All vessels in group	From buildings, boundary, fixed source of ignition		Between vessels
Vessel Water Capacity (litres)	LPG Capacity (kg)	LPG Capacity (kg)	With Fire Wall (Note 1)	No Fire Wall
150 - 500	50 – 250	800	0.3	2.5	1
> 500 - 2500	> 250 – 1100	3500	1.5	3	1
> 2500 - 9000	> 1100 – 4000	12500	4	7.5	1
> 9000 - 135000	> 4000 – 60000	200000	7.5	15	1.5
Notes: / A Fire Wall is intended to protect a vessel from thermal radiation from a nearby fire; and to ensure adequate dispersion for leaking LPG where the distances between the building, boundary or source of ignition are too short to provide adequate dispersion. For vessels up to 1100 kg the fire wall need not be higher than the top of the vessel and may be part of the site boundary. It may also be part of a building wall provided it is imperforate and has 60 minutes fire resistance. See LPG Industry Code of Practice 1. / Weeds long grass and combustible material to be removed from area 6 m or separation distance whichever the smaller. / This table does not apply to Underground and Mounded LPG storage vessels See LPG Industry Code of Practice 1 for further information, including minimum separation distance for vessels of higher capacity.

Table 19.A.2 - Minimum Separation Distances between bulk LPG vessels and other hazards / hazardous substances
Hazard / Hazardous substances		Hazard / Capacity of Hazardous Substance (litres)	LPG storage vessel capacity (tonnes)	Minimum Separation Distance (m)
Hazard / Hazardous Substance
Bulk Flammable Liquids (Flash Point)	< 32°C e.g. Petrol (Class I and some Class II)	-	≤ 60	6 (see Note 1)
			> 60	15 (see Note 1)
	32°C - 65°C e.g. Kerosene, Diesel fuel, Gasoil (Some Class II & some Class III)	≤ 3000	≤ 60	As per Table 18.A1 or 3m, whichever is smaller
			> 60	6 (see Note 1)
		≤ 3000	≤ 60	3 to bund wall or diversion wall and 6 to tank
			> 60	15 to tank, bund wall or diversion wall
Bulk Liquid oxygen		≤ 125000	0.1 - 1.1	6
			> 1.1 - 4	7.5
			> 4 - 60	15
			> 60 - 150	22.5
		(See Note 2)
LPG Evaporation Area(s)		-	-	6 from vessel and/or delivery vehicle
Electricity Cables, including telephone cables		< 1.0 kV	-	1.5 from vertical plane below cable(s)
		≥ 1.0 kV	-	10 from vertical plane below cable(s)
Powered vehicles (see Note 4)		-	-	As per Table 18.A.1 or 6m, whichever is smaller
LPG Cylinders		> 50 kg total quantity; horizontal venting PRV	> 2.2	7.5
			< 2.2	3
		< 300 kg total quantity; vertical venting PRV	-	1
Weeds, long grass, deciduous shrubs, trees, combustible material		_	≤ 1.1	As per Table 18.A1
			> 1.1	6
Notes: / To bund wall. / For large capacities of Liquid oxygen and/or LPG see LPG Industry Code of Practice 1. / The separation distance must be controlled, i.e. no fixed sources of ignition, prohibition on smoking, no vehicles except delivery vessels, all electrical installations to be explosion protected. / This limitation does not apply to LPG delivery vehicles. / PRV = Pressure Relief Valve. / Table 19.A.2 may not apply in full to Underground and Mounded LPG storage vessels - See LPG Industry Code of Practice 1

# Annex B - Bulk LPG Vessel Compound Design Examples.

Figure 19.B.1: Example of Single LPG Vessel Compound Design (<1.1 Tonnes)

Notes:

Fence shall be 1.8 m high

Refer to para 35 for firefighting requirements

No open ducts, drains , gullies to be located within separation distance Annex A (Table 19.A.2).

In unsecured areas (where public has access, e.g. in metered bulk LPG compounds serving Defence Housing Estates) the distance between the vessel wall and fence shall be 3m.

The separation distances shall be adhered to for buildings, site / establishment boundaries and fixed sources of ignition. Weeds, long grass, shrubs and trees should be removed from the area within the separation distance (Tables 19.A.1 & A2 refer), for vessels not exceeding 1.1 Tonnes.

Powered vehicles under the control of the site occupier shall be parked at least 6 m or the separation distance (Tables 19.A.1 / A.2), whichever the smaller, from LPG vessels.

Figure 19.B.2: Example of multiple LPG Vessel Compound Design (>1.1 Tonnes)

Notes:

Fence shall be 1.8 m high

Refer to Part 2 Vol 1 Chapter 19, para 35 for firefighting requirements

No open ducts, drains , gullies to be located within separation distance (Tables 19.A.1/ A.2).

In unsecured areas (where public has access) the distance between the vessel wall and fence shall be 3 m.

The separation distances shall be adhered to for buildings, site / establishment boundaries and fixed sources of ignition. Weeds, long grass, shrubs and trees should be removed to 6m (for larger vessels >1.1 Tonnes).

Powered vehicles under the control of the site occupier shall be parked at least 6 m or the separation distance (Tables 19.A.1 /A.2), whichever the smaller, from LPG vessels.
.
# Annex C - Small Bulk LPG Vessel Adjacent to a Building.

60 minute fire resisting and imperforate
Figure 19.C.1: Example of LPG Vessel adjacent to a building.

# 20 - Bibliography (LPG) Chapters 17,18,19

Chapter Sponsor - DIO TS Eng Gas AH

            1. JSP 317 - Host Page - Joint Service Safety Regulations for the Storage and Handling of
Fuels and Lubricants.

            1. JSP 375 - MOD Health and Safety Handbook.

            1. JSP 850 - JSP 850: Infrastructure and Estate Policy, Standards and Guidance

            1. DSA 03 OME - DSA 03 OME Part 4 Defence Major Accident Control Regulations (MACR).

            1. JSP 515 - MOD Hazardous Stores Information System.

            1. Defence Infrastructure Fire Standards: Defence Infrastructure Fire Standards - Relating to Asset and Property Protection.

            1. Liquid Gas UK: LPG Industry Code of Practice (formerly known as UKLP Code of Practice) 1 - Bulk LPG Storage at Fixed Installations
              1. Part 1: Design, Installation and Operation of Vessels Located Above Ground.
  2. Part 2: Vapour Off-take Small Bulk Propane Installations.
  3. Part3: Examination and Inspection.
  4. Part 4: Buried/Mounded LPG Storage Vessels.

            1. LPG Industry Codes of Practice: LPG Industry Code of Practice (formerly known as UKLP Code of Practice) 3 - Recommendations for Prevention and Control of Fire Involving LPG

            1. LPG Industry Codes of Practice: LPG Industry Code of Practice (formerly known as UKLP Code of Practice) 20 - Liquid LPG Dispensing Facilities

            1. LPG Industry Codes of Practice: LPG Industry Code of Practice (formerly known as UKLP Code of Practice) 22 - Design, Installation and Testing of LPG Piping Systems

            1. LPG Industry Codes of Practice: LPG Industry Code of Practice (formerly known as UKLP Code of Practice) 25 - LPG Central Storage and Distribution Systems for Multiple Consumers

            1. LPG Industry Codes of Practice: LPG Industry Guidance Note (formerly known as UKLP Guidance Note) 3 - A Guide to the preparation of Major Accident Prevention Policies (MAPP's)”

            1. Control of Major Accident Hazard Regulations 2015: UK Statutory Instruments 2015 No. 483, The Control of Major Accident Hazards Regulations 2015

            1. Control of Major Accident Hazards (Amendment): The Control of UK Statutory Instruments 2015 No. 1393, The Control of Major Accident Hazards (Amendment) Regulations 2015

            1. Dangerous Substances: UK Statutory Instruments 1990 No. 304, The Dangerous Substances (Notification and Marking of Sites) Regulations 1990.

            1. Gas Safety: UK Statutory Instruments 1998 No. 2451, The Gas Safety (Installation and Use) Regulations 1998.

            1. Safety Signs and Signals: UK Statutory Instruments1996 No. 341, The Health and Safety (Safety Signs and Signals) Regulations 1996

            1. Health and Safety at Work Act: UK Public General Acts 1974 c. 37, Health and Safety at Work etc. Act 1974

            1. Planning Hazardous Substances: UK Public General Acts 1990 c. 10, Planning (Hazardous Substances) Act 1990

            1. Planning Hazardous Substances Regulations: UK Statutory Instruments 2015 No. 627, The Planning (Hazardous Substances) Regulations 2015

            1. Atmosphere Regulations 2016: UK Statutory Instruments 2016 No. 1107, The Equipment and Protective Systems Intended for Use in Potentially Explosive Atmospheres Regulations 2016

            1. Pressure Systems UK Statutory Instruments 2000 No. 128, The Pressure Systems Safety Regulations 2000.

            1. RIDDOR: UK Statutory Instruments 2013 No. 1471, The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations 2013

            1. The Management of Health & Safety: UK Statutory Instruments 1999 No. 3242, The Management of Health and Safety at Work Regulations 1999.

            1. NIHHSR: UK Statutory Instruments 1982 No. 1357, The Notification of Installations Handling Hazardous Substances Regulations 1982

            1. DSEAR: UK Statutory Instruments 2002 No. 2776, The Dangerous Substances and Explosive Atmospheres Regulations 2002

            1. Control of Major Hazard Regulations: UK Statutory Instruments 1999 No. 981, The Planning (Control of Major-Accident Hazards) Regulations 1999.

            1. BS 4250:2014 - Specification for Commercial Butane and Commercial Propane.

            1. BS EN 3-7:2004+A1:2007 - Portable fire extinguishers. Characteristics, performance requirements and test methods.

            1. BS EN ISO 7010:2020+A1:2020, Graphical symbols. Safety colours and safety signs. Registered safety signs.

            1. BS EN 60079-14:2014, Explosive atmospheres. Electrical installations design, selection and erection.

32. BS EN IEC 60079-0:2018, Explosive atmospheres. Equipment. General requirements.

BS EN 62305-1:2011 - Protection against lightning. General principles.

BS EN 589:2018, Automotive fuels. LPG. Requirements and test methods.

EI Model code of safe practice Part 15: Area classification for installations handling flammable fluids, July 2015.

MOD Form 731 - Equipment Conditioning Label.

UK LPG Code of Practice No 7 - Storage of Full and Empty LPG Cylinders and Cartridges.